## Calculator
|  |  | Solar Calculations |  |  |  | Name C01-01 |  | Rev Orig
2026-08-06
|  |  | Name | Your Address/Location
A |  |  | Nearest City: | Sydney | Nearest Major city |  |  |  | Total Solar KW:
B |  |  | Solar Array 1, 2 KW: | 6.64 | 0 | KW What size solar arrays? |  |  | 6.6KW
|  |  | Array Orientation deg° (Nrth=0) | 20 | 20 | Roof Tilt Angle deg° (from Horizontal)
C |  |  | People in Household: | 2 | people OR | Enter your Loads >> |  | 30 | KWh/day
D |  |  | Planned power use per day: | 14 | KWh/day | Select your Power/Persons profile or Enter own
E |  |  | Flexibility to reduce Power use: | 15 | % | %age you could reduce power use if needed
F |  |  | Nom. Inverter Output Power needed: | 4 | KW | Instantaneous power needed, for a appliances.
G |  |  | Generator Size: | 8 | KVA | Current or planned Generator
H |  |  | 48V Battery size in mind: | 29.952 | KWh | Optional, guide to battery size 1KWh=21Ah |  |  |  | KWh/day | 34.3683 | 31.5759 | 29.1271 | 25.3037 | 21.3352 | 18.3011 | 20.4438 | 25.1318 | 29.5299 | 32.1773 | 32.5425 | 34.2072 | 27.837
[10 empty] | Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Ave
[10 empty] | Solar/Loads | 2.4549 | 2.2554 | 2.0805 | 1.8074 | 1.5239 | 1.3072 | 1.4603 | 1.7951 | 2.1093 | 2.2984 | 2.3245 | 2.4434
MIN.
[24 empty] | 8 | 6.64 | Row.Array1/Equip-Options_SolarArrays
|  | System Configuration | [21 empty] | 1 | 0 | Array2
[24 empty] | 20 | 20 | Array Orientation / Roof Tilt
[24 empty] | 5 | Sydney | City.Row (from calcs/SolarTables)
|  |  | Battery, Loads and System Autonomy | [20 empty] | 2 | Inverter/charger.Row (from calcs/equip)
|  |  | Daily Power Use: | 14 | KWh | KWh you will use per day | [17 empty] | 15 | Battery.Row (from calcs/equip)
|  |  | Inverter Output: | 4 | KW | KW in output, eg 4KW | [17 empty] | FALSE | Enter your own loads
|  |  | Solar Array Summer Output: | 34.3683 | KWH | Solar array total output, KWh
|  |  | Usable Battery Capacity: | 29.952 | KWh | Size of battery, KWh
| Days: | 2.1 nom. | Autonomy: | 2.4 | Days Max | Days of battery, w/o solar Target 2.0-4.0
|  |  | Generator Use Profile: | Infrequent | Use | Size of generator, KVA |  | Battery OK Off-grid
|  |  | Min. Solar output vs Loads: | 1.3072 | Ratio | Target: 1.2 - 1.5 |  | Solar Array OK
Or adjust Orient/Angle
|  |  |  | 415 | W Solar Panel size |  |  | Or decrease people/loads |  |  | Nov: 79.86%; Dec: 20.09% | Loads
|  |  |  | Gel | Battery Type/chemistry | [17 empty] | Used
[21 empty] | Day | Night
Solar Array Size-OK
Notes
A | Cities: Northern cities have higher solar generation than Southern cities | [9 empty] | Mar: System Specification
B | Solar: Solar Array Size should be large enough to provide Solar output greater than daily power use
C | People: Increasing the people in the household usually increases power use | [9 empty] | Jan: 4; Feb: KW+ Inverter; Apr: 1; May: Victron MultiplusII 48/5000/70
D | Daily Power: use should be lower than winter Solar Array output | [8 empty] | Array1 | Jan: 8.12; Feb: KW Max. Solar; Apr: 1; May: SmartSolar MPPT 450/100 Tr
E | Flexibility: in daily power use, will allow you to use a smaller Battery Bank, and/or less Generator use | [8 empty] | Array2 | Feb: KW Max. Solar; Apr: 0
F | Inverter Power: should be greater than largest appliance power rating | [9 empty] | Jan: 29.952; Feb: KWh Battery; Apr: 24; May: GNB 676Ah Gel
G | Generator Use: <1.5days Batt.storage = Frequent; 1.5-2.5=Occasional; 2.5> = Rare Use | [8 empty] | Array1 | Jan: 6.64; Feb: KW Solar Array; Apr: 16; May: Trina 415W Mono PERC Solar Panels
H | Battery Capacity: should cover 3 days power use, or generator will be used more | bar: Feb to Mar; May to Dec
| Systems are 48V Battery banks, although similar for 24V or other voltages | [9 empty] | Jan: 6.64; Feb: KW Array, total; Apr: 1; May: E30 Energy Controller/Dashboard
[14 empty] | 1 | Battery monitor BMV 702 - Bluetooth Victron
Tips | [10 empty] | Apr: 1; May: Control Victron Temperature sensor for BMV-702/712
https://www.yourhome.gov.au/passive-design | [10 empty] | Apr: 1; May: DC Bus Enclosure
Add your own solar data, Calcs Worksheet, for your location: http://www.bom.gov.au/climate/data/ | [10 empty] | Apr: 1; May: Solar isolator, cables, joiners
[14 empty] | 1 | Battery Cables, Lugs, Fuses
Calculation Sheet Rev 4.0
Nom.Power Limit
Peak Power Limt
Max.Daily Peak

## Loads (hidden)
[10 empty] | Address: |  | 2026-08-06
|  |  | Loads & Equipment | [8 empty] | Your Address/Location
|  |  | Name C01-02 |  | Rev Orig |  |  |  |  | Job# | Name | (See disclaimer)
C.Myatt
| ecoCool Pty Ltd | [9 empty] | Battery Effic. | 0.95
[11 empty] | Inverter Effic. | 0.96
| Time | Load profile | Fridge/Fr | Pump | Light | TV | Cooking | Lighting | Appli-ances | System & Comp | Total | Total Effic. |  | Peak Load Calculations | [5 empty] | Daytime Peak:
|  | % of total | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | 0.95033 | 0.039932 | Ave.Load | Nom.Load | Load+30% | Load+50% | Load.Peak | Load.Peak
Night | Total | 100% | 1.68 | 5 | 4 | 0.52 | 0.8 | 0.34 | 1.4 | 0.96 | 14.7 | 15.5 |  | W | W | W | W | W | W
| 12am | 1% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 | KWh/day Summer |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 12am
| 1am | 1% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 | 15.5 |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 1am
| 2am | 1% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 | KWh/day Winter |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 2am
| 3am | 1% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 | 100% |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 3am
| 4am | 1% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 | A/C WinterFraction |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 4am
| 5am | 1% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 | KWh Daytime use |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 5am | AC PV: | 0
Day | 6am | 10% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 | 12.3535 |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 6am | Fraction: | 0.65
| 7am | 10% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.04 | 0.21 | 79.86% |  | 0.21 | 4 | 5.2 | 6 | 9 | 9 | 0.336 | 7am
| 8am | 3% | 0.07 | 1 | 0 | 0 | 0.1 | 0 | 0.1 | 0.04 | 1.31 |  |  | 1.31 | 4 | 5.2 | 6 | 9 | 9 | 2.096 | 8am
| 9am | 1% | 0.07 | 1 | 0.5 | 0 | 0 | 0 | 0.1 | 0.04 | 1.71 |  |  | 1.71 | 4 | 5.2 | 6 | 9 | 9 | 2.736 | 9am
| 10am | 1% | 0.07 | 1 | 0.5 | 0 | 0 | 0 | 0.2 | 0.04 | 1.81 |  |  | 1.81 | 4 | 5.2 | 6 | 9 | 9 | 2.896 | 10am
| 11am | 8% | 0.07 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0.04 | 1.61 |  |  | 1.61 | 4 | 5.2 | 6 | 9 | 9 | 2.576 | 11am
| 12pm | 8% | 0.07 | 1 | 0.5 | 0 | 0.15 | 0 | 0 | 0.04 | 1.76 |  |  | 1.76 | 4 | 5.2 | 6 | 9 | 9 | 2.816 | 12pm
| 1pm | 1% | 0.07 | 0 | 0.5 | 0 | 0 | 0 | 0.05 | 0.04 | 0.66 |  |  | 0.66 | 4 | 5.2 | 6 | 9 | 9 | 1.056 | 1pm
| 2pm | 1% | 0.07 | 0 | 0.5 | 0 | 0 | 0 | 0.25 | 0.04 | 0.86 |  |  | 0.86 | 4 | 5.2 | 6 | 9 | 9 | 1.376 | 2pm
| 3pm | 1% | 0.07 | 0 | 0.5 | 0 | 0 | 0 | 0.25 | 0.04 | 0.86 |  |  | 0.86 | 4 | 5.2 | 6 | 9 | 9 | 1.376 | 3pm
| 4pm | 1% | 0.07 | 0 | 0.5 | 0 | 0 | 0 | 0.05 | 0.04 | 0.66 |  |  | 0.66 | 4 | 5.2 | 6 | 9 | 9 | 1.056 | 4pm
| 5pm | 7% | 0.07 | 0 | 0 |  | 0 | 0.02 | 0.05 | 0.04 | 0.18 | KWh Night use |  | 0.18 | 4 | 5.2 | 6 | 9 | 9 | 0.288 | 5pm
Night | 6pm | 12% | 0.07 | 0 | 0 | 0.13 | 0.15 | 0.02 | 0 | 0.04 | 0.41 | 3.1147 |  | 0.41 | 4 | 5.2 | 6 | 9 | 9 | 0.656 | 6pm
| 7pm | 12% | 0.07 | 0 | 0 | 0.13 | 0.2 | 0.1 | 0.15 | 0.04 | 0.69 | 20.09% |  | 0.69 | 4 | 5.2 | 6 | 9 | 9 | 1.104 | 7pm
| 8pm | 9% | 0.07 | 0 | 0 | 0.13 | 0.2 | 0.1 | 0.1 | 0.04 | 0.64 |  |  | 0.64 | 4 | 5.2 | 6 | 9 | 9 | 1.024 | 8pm
| 9pm | 5% | 0.07 | 0 | 0 | 0.13 | 0 | 0.1 | 0 | 0.04 | 0.34 |  |  | 0.34 | 4 | 5.2 | 6 | 9 | 9 | 0.544 | 9pm
| 10pm | 3% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 |  |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 10pm
| 11pm | 1% | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.11 |  |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 11pm
|  | 100% | 1.68 | 5 | 4 | 0.52 | 0.8 | 0.34 | 1.4 | 0.96 | 14.7 |  |  | 0.11 | 4 | 5.2 | 6 | 9 | 9 | 0.176 | 12pm
Notes:
HW Gas & 1 x Fridges, computer, router, LED lights, power. 3 Phase. Cooking from Gas, Added also: 4 x Air conditioners, 8KW Generator See below
Equipment Ratings
[8 empty] | % | W
|  |  | KWh/hr | KWh/d | KWh/yr | W | A | DutyCyc. | Start.Pk | Startup.X | Comment
| TV-LED |  | 0.023 | 0.552 |  | 92 |  | 6
| Fridge500L |  | 0.057078 | 1.3699 | 500 | 199.2 | 0.83 | 14.54% | 1195.2 | 6
| Freezer280L |  | 0.040183 | 0.96438 | 352 | 180 | 0.75 | 18.66% | 1080 | 6 | eg Westinghouse 280L
| Washing Machine |  | 0.0045833 | 0.11 |  | 220 |  | 0.5 | 1540 | 7 | Very small consum., 1.5KW Surge
| Phone charger x 2 |  | 0.0025 | 0.06 |  | 5 |  | 12
| Lights, LED |  | 0.02375 | 0.57 |  | 95 |  | 6 | 450 |  | 450W all lights on
| Computer |  | 0.25
| Router |  | 0.04
| System Self power |  | 0.09 | [7 empty] | 30W approx/constant
| Air Con x 5 units |  | 1.71 | 41.04 |  | 5330
| Kitchen appliance |  | 0.0083333 | 0.2 |  | 1000 |  | 0.2 |  |  | eg. Microwave
| Air Con Winter |  |  | 30-40%
| Ceiling Fans |  | 0.04 |  |  | 40
| Pool Pump |  |  |  |  | 1100 |  |  |  |  | 1HP, 1.5HP = 1.65KW
Surge Calculations
Surge Power (MultiplusII 48/5000/70):
| Max Load: | 4 | KW | From User.profiles
| Nom. Pwr: | 4 | KW | Nom.@25C*
| 130% over: | 5.2 | KW | 30 mins.
| 150% over: | 6 | KW | 5 sec.
| Peak: | 9 | KW | 0.5 sec.
Temperature
|  |  | BOM mean Max Mins, for: |  |  | Sydney
Ave | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Max T. C | 26.7 | 26.5 | 25.4 | 23 | 20.2 | 17.7 | 17.2 | 18.5 | 20.7 | 22.7 | 24.2 | 25.9 |  | 21 | Spring.Ave-Max
Min T. C | 19 | 19.2 | 17.7 | 14.4 | 11.1 | 8.8 | 7.4 | 8.3 | 10.6 | 13.4 | 15.5 | 17.6 |  | 8 | Winter.Min
|  | Brisbane Airport | BOM mean Max Mins, 2022 year, annual mean
Brisbane.max | 29.1 | 29 | 28.1 | 26 | 23.6 | 21.3 | 20.9 | 22 | 24.2 | 25.5 | 26.9 | 28.2 |  | 24 | Spring.Ave-Max
Brisbane.min | 21.4 | 21.2 | 19.8 | 16.5 | 13 | 10.8 | 9.3 | 9.8 | 12.9 | 15.9 | 18.3 | 20.2 |  | 10 | Winter.Min
|  | Canberra Airport | BOM mean Max Mins, 2022 year, annual mean
Canberra.max | 30.2 | 27.9 | 25 | 20.8 | 16.4 | 13.3 | 12.7 | 14.1 | 17.9 | 21.2 | 24.7 | 27.2 |  | 18 | Spring.Ave-Max
Canberra.min | 14.2 | 13.4 | 11.2 | 6.9 | 2.4 | 1.1 | 0.1 | 1 | 3.2 | 6.3 | 9.7 | 11.9 |  | 1 | Winter.Min
|  | Darwin Airport | BOM mean Max Mins, 2022 year, annual mean
Darwin.max | 31.8 | 31.5 | 32 | 32.8 | 32.1 | 30.7 | 30.7 | 31.5 | 32.7 | 33.3 | 33.4 | 32.7 |  | 33 | Spring.Ave-Max
Darwin.min | 24.9 | 24.8 | 24.6 | 24.1 | 22.2 | 20 | 19.3 | 20.3 | 23 | 24.9 | 25.3 | 25.3 |  | 20 | Winter.Min
|  | Hobart Airport | BOM mean Max Mins, 2022 year, annual mean
Hobart.max | 22.7 | 22.3 | 20.9 | 18.2 | 15.3 | 13 | 12.6 | 13.5 | 15.5 | 17.4 | 19.1 | 20.8 |  | 16 | Spring.Ave-Max
Hobart.min | 12.2 | 12.1 | 10.9 | 8.8 | 6.7 | 4.7 | 4.2 | 4.8 | 6.1 | 7.6 | 9.3 | 10.9 |  | 5 | Winter.Min
|  | Sydney Airport | BOM mean Max Mins, 2022 year, annual mean
Sydney.max | 26.7 | 26.5 | 25.4 | 23 | 20.2 | 17.7 | 17.2 | 18.5 | 20.7 | 22.7 | 24.2 | 25.9 |  | 21 | Spring.Ave-Max
Sydney.min | 19 | 19.2 | 17.7 | 14.4 | 11.1 | 8.8 | 7.4 | 8.3 | 10.6 | 13.4 | 15.5 | 17.6 |  | 8 | Winter.Min
|  | Melbourne Airport | BOM mean Max Mins, 2022 year, annual mean
Melbourne.max | 26.7 | 25.9 | 24.1 | 20.2 | 16.4 | 13.8 | 13.2 | 14.4 | 16.9 | 19.5 | 21.9 | 24.6 |  | 17 | Spring.Ave-Max
Melbourne.min | 13.8 | 14.1 | 12.7 | 10.1 | 7.9 | 6.1 | 5.4 | 5.8 | 6.9 | 8.4 | 10.2 | 12 |  | 6 | Winter.Min
|  | Adelaide Airport | BOM mean Max Mins, 2022 year, annual mean
Adelaide.max | 28.2 | 28 | 25.5 | 22.3 | 18.6 | 15.9 | 15 | 16 | 18.3 | 21.2 | 24 | 25.9 |  | 18 | Spring.Ave-Max
Adelaide.min | 16.2 | 16.2 | 14.6 | 11.9 | 9.7 | 7.7 | 7.1 | 7.6 | 9 | 10.8 | 12.9 | 14.7 |  | 8 | Winter.Min
|  | Alice Springs Airport | BOM mean Max Mins, 2022 year, annual mean
Alice Springs.max | 36.4 | 35.2 | 32.9 | 28.4 | 23.1 | 19.9 | 19.9 | 22.8 | 27.4 | 31.2 | 33.7 | 35.5 |  | 27 | Spring.Ave-Max
Alice Springs.min | 21.6 | 20.7 | 17.6 | 12.6 | 8.1 | 4.9 | 3.9 | 5.9 | 10.3 | 14.8 | 17.9 | 20.3 |  | 4 | Winter.Min
|  | Perth Airport | BOM mean Max Mins, 2022 year, annual mean
Perth.max | 31.8 | 32 | 29.8 | 25.7 | 21.8 | 19 | 18 | 18.6 | 20.3 | 22.8 | 26.1 | 29.2 |  | 20 | Spring.Ave-Max
Perth.min | 17.1 | 17.6 | 16 | 13 | 10.4 | 9 | 8.1 | 8.1 | 8.9 | 10.3 | 12.8 | 15 |  | 9 | Winter.Min
|  | Cairns Airport | BOM mean Max Mins, 2022 year, annual mean
Cairns.max | 31.5 | 31.3 | 30.6 | 29.4 | 27.7 | 26.1 | 25.8 | 26.7 | 28.2 | 29.6 | 30.8 | 31.5 |  | 28 | Spring.Ave-Max
Cairns.min | 23.7 | 23.8 | 23.1 | 21.7 | 20 | 18 | 17.2 | 17.4 | 18.8 | 20.7 | 22.3 | 23.4 |  | 18 | Winter.Min
Note on J7: Includes: battery constraints and efficiency losses

## Version
Version History
4 | Published Version, configurable options with user-dropdowns/scroll-options & Label refinements
1-3.2 | Original Internal versions

## -calcs- (hidden)
| ecoCool Pty Ltd |  |  |  | 2026-08-06
| Array 1 Calculations |  |  | Name | Your Address/Location
(See disclaimer)
Rev 0 | Element | Value | Units | Units info | Comments
Array2 | Array size selected: | 6.64
Solar | Number of Solar Panels | 16
| Brand | Trina |  |  | Per AS5033: 2014 |  |  |  | Array1 |  |  |  |  | Solar Calculations | [7 empty] | Revision: | Orig | Name
| Part # | TSM-DE09R.08 | [6 empty] | Installation Details |  | Option 1 | [12 empty] | Your Address/Location
| Maximum Power at STC (Pmax) | 415 | W | [5 empty] | Azimuth |  | 20
| Optimum Operating Voltage (Vmp) | 41.7 | V dc | [5 empty] | Tilt |  | 20 | [12 empty] | Comments
| Optimum Operating Current (Imp) | 9.94 | A | [5 empty] | System Size |  | 6640 | W
| Open Circuit Voltage VOC | 50 | V dc | [5 empty] | Panels | 16 | 415 | W
| Short Circuit Current (Isc) | 10.55 | A | [5 empty] | Sydney | #N/A | Lookup: Azimuth + LocationSolarTable + RoofAngle | [13 empty] | 2026-08-06
| Module Efficiency | 20.8 | % |  |  |  |  | 0.05 | 95% | Efficiency derating | [14 empty] | Craig Myatt
| Maximum Series Fuse Rating | 20 | A |  | Imodmax ocpr | AS5033-2014 1.4 |  | 0.03 | 97% | Soiling derated %age | [14 empty] | ecoCool Pty Ltd |  |  | #N/A
| Power Tolerance | 5 | W +/- |  |  |  |  | -0.0034 | 95.24% | Temperature derating | [14 empty] | www.ecocool.com.au |  |  | #N/A
| Temperature Coefficient of Voc | -0.25 | %/°C | [5 empty] | Battery Size |  | 29.952 | KWh | [12 empty] | info@ecocool.com.au |  |  | #N/A |  | Sydney | 100% | 105% | 113% | 124% | 137% | 142% | 141% | 130% | 117% | 107% | 101% | 98%
| Temperature Coefficient of Pmax | -0.34 | %/°C | [5 empty] | (NOCT=43C) | [17 empty] | #N/A | #N/A |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Test Temp @ STC | 25 | DegC | [9 empty] | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |  | #N/A | #N/A |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Length | 1762 | mm | [5 empty] | Location Multiplier |  |  |  | 100% | 105% | 113% | 124% | 137% | 142% | 141% | 130% | 117% | 107% | 101% | 98% |  |  | #N/A | #N/A |  | Loc. Mult: | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Width | 1134 | mm | [5 empty] | Estimated Performance |  |  |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Ave |  | #N/A | #N/A |  |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Ave
| Thickness | 30 | mm | [5 empty] | PSH for Sydney at tilt 20 and azimuth 20 |  |  |  | 6.4 | 5.6 | 4.8 | 3.8 | 2.9 | 2.4 | 2.7 | 3.6 | 4.7 | 5.6 | 6 | 6.5 | 4.6 |  | #N/A | #N/A
| Weight | 21.8 | kg | [5 empty] | Estimated Daily KWh production |  |  |  | 39.1601 | 35.9783 | 33.1882 | 28.8316 | 24.3098 | 20.8527 | 23.2941 | 28.6358 | 33.6471 | 36.6636 | 37.0797 | 38.9765 | 31.7181 |  | #N/A | #N/A |  | PSH- | 6.3 | 5.5 | 4.6 | 4.1 | 3.4 | 2.9 | 3.2 | 4.1 | 4.9 | 5.6 | 6.1 | 6 | 5.1
| Number of Panels/String | 8 | [6 empty] | Percentage of full sun |  |  |  | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 87.76% | 92.15% |  | #N/A | #N/A
| Number of Strings | 2 | [5 empty] | Array1 | Est Daily KWh production, shading+derating |  |  |  | 34.3683 | 31.5759 | 29.1271 | 25.3037 | 21.3352 | 18.3011 | 20.4438 | 25.1318 | 29.5299 | 32.1773 | 32.5425 | 34.2072 | 29.2282 |  | #N/A | #N/A |  |  |  | For Peak Sun Hours (PSH) for your location, to go http://www.bom.gov.au/climate/data/
| Spring Ave Max Temp | 21 | DegC | 14 bel. NOCT | (NOCT=43C) |  |  | Array 1+2 | Est Daily KWh production, shading+derating |  |  |  | 34.3683 | 31.5759 | 29.1271 | 25.3037 | 21.3352 | 18.3011 | 20.4438 | 25.1318 | 29.5299 | 32.1773 | 32.5425 | 34.2072 | 29.2282 |  | #N/A | 34.2072
| Winter Min. Temp | 5 | DegC | Loc. - 3C | [8 empty] | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 | 29.2282 |  | #N/A | Solar.Label | Solar Tables lookups |  |  | Get: Daily global solar exposure, in KWH m-2 (Use "mean" for all years)
| String VOC | 400 | V dc |  |  |  |  | KWh/Mon | Current Bill / month |  |  |  | 441.3315 | 402.1812 | 441.3315 | 377.2161 | 389.79 | 402.1556 | 415.5608 | 415.5608 | 389.79 | 377.2161 | 427.095 | 441.3315 |  |  | #N/A
| PV Array Max. Volts | 440 |  |  | Voc+y(Tmin-Tstc)M | AS5033-2014 4.2 |  | 425.8333 | Total Daily usage (KWh) |  |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  |  | 14 | A | AD212:AE223 | Location-Main
| Array Power | 6640 | W |  | Voc=ModuleVOC; y=Voltage Temp Coef.V/°C; |  |  | 14 | Average Usage during Day (KWh) |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  | Load.Label | B | AD212:AE223 | City1
| String O/Current Protection? | No | Yes/No | 10.55 | ((Sa-1)xIscmod) > Imodmax ocpr | AS5033-2014 3.3.4 |  | KWh/day | Average Usage during night (KWh) |  |  |  | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 |  |  |  | C | #N/A | City2
| String Fuse Min | 15.825 | A |  | In > 1.5 x Isc mod | AS5033-2014 3.3.5 |  |  | Daily charge |  |  |  | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998
| String Fuse Max | 20 | A |  | In < 2.4 x Isc mod | AS5033-2014 3.3.5 |  | 26.74% | FIT rate |  |  |  | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 336.1249 | Solar Index
| Fuse Size | 20 | A | MCB 350V min DC rated (Noark) |  |  |  | Night | $ per KWh rate/s DAY |  |  |  | 0.4925 | 0.4925 | 0.4925 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.4925 | 0.4925
| Solar Controller | 21 | # | SmartSolar MPPT 450/100 Tr |  |  |  | 73.26% | $ per KWh rate/s NIGHT |  |  |  | 0.26685 | 0.26685 | 0.26685 | 0.23138 | 0.23138 | 0.2621 | 0.2621 | 0.2621 | 0.23138 | 0.23138 | 0.26685 | 0.26685 |  | Off Grid?
| Solar Controller Max PV | 4000 | W | (See VE-MPPT Calc Spreadsheet for calcs) |  |  |  | Night | Daily Cost of Power - without system |  |  |  | 14.2365 | 14.2365 | 14.2365 | 12.5739 | 12.5739 | 13.4052 | 13.4052 | 13.4052 | 12.5739 | 12.5739 | 14.2365 | 14.2365 |  | Yes
| Location (from tables) | Sydney |  |  | %age from 1st Location, to second |  |  |  | Daily Cost of Power - with system |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Battery?
| Min PSH for location | 2.4 |  |  | Your Location, PSH data, AF23:AR34 |  |  |  | Daily Feed-in Ret |  | 13.6723 | Ave /mo | 0.33833 | 0.72625 | 0.66992 | 0.58198 | 0.49071 | 0.42093 | 0.47021 | 0.57803 | 0.67919 | 0.035978 | 0.086371 | 0.3161 | 0.4495 | Yes
| Shading/Efficiency/Soiling | 95% | [6 empty] | Daily net $ (+pay -paid) |  |  |  | -0.33833 | -0.72625 | -0.66992 | -0.58198 | -0.49071 | -0.42093 | -0.47021 | -0.57803 | -0.67919 | -0.035978 | -0.086371 | -0.3161 | -0.4495
| Solar panel roof tilt from 0 | 20 | [6 empty] | Monthly net $ |  | 13.6056 |  | -10.4883 | -20.3349 | -20.7676 | -17.4595 | -15.212 | -12.6278 | -14.5764 | -17.919 | -20.3756 | -1.1153 | -2.5911 | -9.7991 | -13.6056 | $pay
| Solar aspect (azimuth) | 20 | [6 empty] | Savings |  | 423.6522 | Ave /mo | 451.8199 | 422.516 | 462.0992 | 394.6756 | 405.002 | 414.7833 | 430.1372 | 433.4797 | 410.1656 | 378.3314 | 429.6861 | 451.1307 | 5083.8268 | $Savings
[9 empty] | Payback period |  | 0 | Years | 0 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268
| Battry Bank Size Selected: | 29.952 | KWh | [5 empty] | NPV of system |  | 61005.9212 | 12 yrs | 0 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268 | 5083.8268
Battery | Number of Batteries | 24 |  |  | Per AS2676.2: 1992 |  |  |  | FIT rate |  | 0.115 | Int.rate | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Type | Gel | [6 empty] | total System price: |  | 0 | 0% | 0: Year from Installation >>>>
| Part # | GNB 676Ah Gel | [10 empty] | 0: 30.4167; 1: days/mo
| Module AH (20hr) | 624 | AH |  |  |  |  | w/Batt | Grid Use-night KWh (GR.N) |  |  |  | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806
| Module Nominal Voltage | 2 | Vdc | [5 empty] | Battery Discharge Night KWh (BD) |  |  |  | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019
| Strings | 1 | [6 empty] | Battery Recharge Day KWh (BR) |  |  |  | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999
| Modules/string | 24 | [5 empty] | w/Batt | Grid Use-day KWh (GR.D) |  |  |  | 6.8737 | 6.7241 | 9.1728 | 12.9963 | 16.9647 | 19.9988 | 17.8562 | 13.1681 | 8.77 | 6.4355 | 6.5085 | 6.8414
| Bank Nominal voltage | 48 | Vdc | [5 empty] | Feed-In Day (FI) KWh |  |  |  | 2.942 | 6.3152 | 5.8254 | 5.0607 | 4.267 | 3.6602 | 4.0888 | 5.0264 | 5.906 | 0.31285 | 0.75105 | 2.7487
| Max. Voltage | 57.6 | Vdc | [5 empty] | Add Grid-use night* |  |  | Total KWh usage | 1: 980; 2: 32.2192; 3: 6.4438; 4: 25.7753; 8: #REF!; 9: $ per KWh rate/s
| Max DOD | 100% | DOD | [5 empty] | Grid use day w/o Batt later |  |  | Daily charge | 1: 1.24; 2: per day; 3: 1.24; 8: #VALUE!; 9: Daily Cost of Power - without system
| Nominal DOD | 80% | DOD | [8 empty] | Rate per KWh | 1: 0.2662; 2: per KWh; 3: 0.2662; 8: #VALUE!; 9: Daily Cost of Power - with system
| Bank Ah Capacity | 624 | Ah | [8 empty] | Seniors discount: | 1: 0.932; 2: per day; 3: 340; 4: per yr; 8: 30177.3687; 9: Daily Feed-in Returned
| Module Nominal Capacity | 1.248 | KWh | [8 empty] | Days of Bill | 1: 96; 2: days
| Bank Full Capacity | 29.952 | KWh | [8 empty] | Usage charge | 1: 260.876; 8: Commercial Rates (energy Aus); 12: Batt Effic. | 0.94
| BankUsable Capacity | 29.952 | KWh | C | [7 empty] | Supply charge | 1: 119.0429; 3: 0%; 4: General discount; 9: Peak; 10: 0.5709; 12: C | 0.2
| Nom. Output | 83.3333 | A | 0.13355 | #N/A | [7 empty] | 3: 1.24; 4: Discounted Daily usage rate; 9: Shoulder; 10: 0.3531; 12: CN | 0.03
| Peak. Output | 187.5 | A | 0.30048 | #N/A | [6 empty] | #1 Discount | 3: 1.9998; 4: Commercial Daily usage rate; 9: Off-peak; 10: 0.2189
| Peak. Output | 9000 | W |  | 15sec | [6 empty] | #1 Discount | 3: 0.35; 4: Day Rate KWh (pro rataed)
| Life Cycles | 4000 | Cycles |  | @25degC | [6 empty] | #1 Discount | 3: 0.29; 4: Night Rate KWh (pro rataed); 8: LD; 9: Loads-day; 10: 10; 11: KWh; 12: 7a-5pm
| End of life | 10.9589 | Years | [9 empty] | 3: 0.5709; 4: Peak KWh rate; 8: LN; 9: Loads-night; 10: 27.4; 11: KWh; 12: 5p-7am
| Battery String Fault Current | 4050 | A | 35 | AGM FC Factor | [6 empty] | Total Bill | 1: 379.9189; 3: 0.3531; 4: Shoulder KWh rate; 10: 37.4
| Battery Bank Fault Current | 4050 | A | 35 | AGM FC Factor | [7 empty] | 3: 0.2189; 4: Off-Peak KWh rate
| Min. Cable Size to fuse | #NAME? | mm | [9 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Target Max Voltage drop | 3 | % | [8 empty] | KWh $ - Day | 0.4925 | 0.4925 | 0.4925 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.4925 | 0.4925
| Distance of Wire Run | 2 | m | [8 empty] | KWh $ - Night | 0.26685 | 0.26685 | 0.26685 | 0.23138 | 0.23138 | 0.2621 | 0.2621 | 0.2621 | 0.23138 | 0.23138 | 0.26685 | 0.26685
| Peak Supply Current | 195.3125 | A | [9 empty] | Feb: Energy Australia Commercial Rates, 2020; Off-Peak KWh rate Jun: (Pro-rataed, based on set day/nigth hours, see CalcsA sheet)
| Resistance | 0.0014496 | Ohms | [8 empty] | Cost of power no system: | 14.2365 | 14.2365 | 14.2365 | 12.5739 | 12.5739 | 13.4052 | 13.4052 | 13.4052 | 12.5739 | 12.5739 | 14.2365 | 14.2365
| Cable Area | 2.5e-05 | m2
| Voltage Drop-V | 0.28313 | V
| Voltage Drop-% | 0.5899%
| Inverter Size Selected: | 4 | KW
Inverter | Nominal Output | 5000 | VA
| Brand | Victron
| Part # | MultiplusII 48/5000/70 |  |  | See Datasheet | [5 empty] | PVC 90C |  | Feb: Rubber 110C; Mar: Rubber 110C; 0.2189 Apr: PVC 90C
| Nominal Voltage | 48 | V |  | Volts DC | [5 empty] | Current |  | Jan: Wire Size; Feb: Current; Mar: Fault; 0.2189 Apr: Fault; Off-Peak KWh rate May: Auto Size; Off-Peak KWh rate Jun: OD; Off-Peak KWh rate Jul: (* From Chrisensen battery handout)
| Max. Output | 9 | KW |  | Maximum output, usually for short time | [5 empty] | Capacity A | Fault A | Jan: mm2; Feb: Capacity A; Mar: Current; 0.2189 Apr: Current; Off-Peak KWh rate Jul: WW Calculator (Bambach)
| Nominal Output | 4 | KW |  | Nominal output, sustainable over time. | [5 empty] | 54 | 1790 | Jan: 10; Feb: 102; Mar: 1790; 0.2189 Apr: 1460
| Efficiency | 0.96 |  |  | 0.96 = 95% efficient | [5 empty] | 63 | 2327 | Jan: 13; Feb: 63; Mar: 2327; 0.2189 Apr: 1898; Off-Peak KWh rate May: 6B&S
[11 empty] | 72 | 2864 | Jan: 16; Feb: 135; Mar: 2864; 0.2189 Apr: 2336; Off-Peak KWh rate Jul: *current carrying capacity (bundle x 3/conduit)
Energy | Occupancy cycle | 7 | days/wk |  | Per AS4509.2: 2010 | [5 empty] | 85 | 2958 | Jan: 20.26; Feb: 85; Mar: 2958; 0.2189 Apr: 2958; Off-Peak KWh rate May: 4B&S; Off-Peak KWh rate Jun: 8.3mm; Off-Peak KWh rate Jul: http://wirewizard.bambachcables.com.au/
| Estimated usage KWh/day | 14 | KWh/day | Nominal power draw | [6 empty] | 97 | 4475 | Jan: 25; Feb: 178; Mar: 4475; 0.2189 Apr: 3650; Off-Peak KWh rate May: 3B&S (26.45mm); Off-Peak KWh rate Jul: 25mm Current carrying cap = 124A, 75DegC single, 151A, 90DegC single
| Estimated usage KWh/day | 14 | KWh/day | Winter min | [6 empty] | 119 | 6265 | Jan: 35; Feb: 221; Mar: 6265; 0.2189 Apr: 5110
| Max KW | 3 | KW | Maximum Power draw, instantaneous | [7 empty] | 5774 | Jan: 39.55; Feb: 130; Mar: 5774; 0.2189 Apr: 5774; Off-Peak KWh rate May: 1B&S
| Min Solar - Winter | 2.4 | PSH | Sydney | [6 empty] | 146 | 8950 | Jan: 50; Feb: 279; Mar: 8950; 0.2189 Apr: 7300; Off-Peak KWh rate May: 0B&S (49mm)
| Max Solar - Summer | 6.5 | PSH | Sydney | [6 empty] | 184 | 12530 | Jan: 70; Feb: 351; Mar: 12530; 0.2189 Apr: 10220
| Min Energy Production | 13.7687 | KWh/day | 0.9 | Panel fouling factor | [5 empty] | 230 | 16110 | Jan: 95; Feb: 422; Mar: 16110; 0.2189 Apr: 13870
| Max Energy Production | 37.2902 | KWh/day | 0.9 | Panel fouling factor | [5 empty] | 267 | 21480 | Jan: 120; Feb: 500; Mar: 21480; 0.2189 Apr: 17520
| 3 days Energy Use | 42 | KWh | [9 empty] | Mar: (Note Special Design Separation, over 20KA)
|  | 2.1 | Days of 3day Battery capacity needed | [9 empty] | Jan: Gauge Guide
| Estimated usage KWh/day MIN. | 12.3958 | KWh/day | [9 empty] | Jan: Auto Size; Feb: Nom Area mm2; Mar: Nom O.D.mm; 0.2189 Apr: Amp Rating; Off-Peak KWh rate May: Part # Prefix
| 3 days Energy Use min. | 37.1875 | KWh | [9 empty] | Jan: 8 B&S; Feb: 7.71; Mar: 5.5; 0.2189 Apr: 74; Off-Peak KWh rate May: C8
|  | 2.4 | Days of 3day Battery capacity needed | [9 empty] | Jan: 6 B&S; Feb: 13.5; Mar: 7.2; 0.2189 Apr: 103; Off-Peak KWh rate May: C6
[13 empty] | 4 B&S | 20.26 | 8.3 | 135 | C4
[13 empty] | 3 B&S | 26.45 | 10.2 | 168 | C3
[13 empty] | 2 B&S | 32.07 | 11.3 | 188 | C2
[13 empty] | 1 B&S | 39.55 | 12.1 | 210 | C1
[13 empty] | 0 B&S | 49 | 12.7 | 246 | C0
| ecoCool Pty Ltd |  |  |  | 2026-08-06
| Array 2 Calculations |  |  | Name | Your Address/Location
(See disclaimer)
Rev 0 | Element | Value | Units | Units info | Comments
Array1 | Array size selected: | 0 | [7 empty] | C192:M227
Solar | Number of Solar Panels | 0
| Brand | #N/A |  |  | Per AS5033: 2014 |  |  |  | Array 2 |  |  |  | Feb: Solar Calculations; Off-Peak KWh rate Oct: Revision:; Off-Peak KWh rate Nov: A; Off-Peak KWh rate Dec: Name
| Part # | #N/A | [6 empty] | Installation Details |  | Option 1 |  | Off-Peak KWh rate Dec: Your Address/Location
| Maximum Power at STC (Pmax) | 0 | W | [5 empty] | Azimuth |  | 20
| Optimum Operating Voltage (Vmp) | 0 | V dc | [5 empty] | Tilt |  | 20 |  | Off-Peak KWh rate Dec: Comments
| Optimum Operating Current (Imp) | 0 | A | [5 empty] | System Size |  | 0 | W
| Open Circuit Voltage VOC | 0 | V dc | [5 empty] | Panels | 0 | 0 | W
| Short Circuit Current (Isc) | 0 | A | [5 empty] | Sydney | #N/A | [14 empty] | 2026-08-06
| Module Efficiency | 0 | % |  |  |  |  | 0.05 | 95% | Efficiency derating | [14 empty] | Craig Myatt
| Maximum Series Fuse Rating | 0 | A |  | Imodmax ocpr | AS5033-2014 1.4 |  | 0.03 | 97% | Soiling derated %age | [14 empty] | ecoCool Pty Ltd
| Power Tolerance | 0 | W +/- |  |  |  |  | 0 | 100% | Temperature derating | [14 empty] | www.ecocool.com.au
| Temperature Coefficient of Voc | 0 | %/°C | y |  |  |  |  | Battery Size |  | 29.952 | KWh | [12 empty] | info@ecocool.com.au |  |  |  |  | Sydney | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Temperature Coefficient of Pmax | 0 | %/°C
| Test Temp @ STC | 0 | DegC | [9 empty] | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Length | 0 | mm | [5 empty] | Location Multiplier |  |  |  | 100% | 105% | 113% | 124% | 137% | 142% | 141% | 130% | 117% | 107% | 101% | 98% | [5 empty] | Loc. Mult: | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Width | 0 | mm | [5 empty] | Estimated Performance |  |  |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Ave | [5 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Ave
| Thickness | 0 | mm | [5 empty] | PSH for Sydney at tilt 20 and azimuth 20 |  |  |  | 6.4 | 5.6 | 4.8 | 3.8 | 2.9 | 2.4 | 2.7 | 3.6 | 4.7 | 5.6 | 6 | 6.5 | 4.6
| Weight | 0 | kg | [5 empty] | Estimated Daily KWh production |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | PSH- | 6.3 | 5.5 | 4.6 | 4.1 | 3.4 | 2.9 | 3.2 | 4.1 | 4.9 | 5.6 | 6.1 | 6 | 4.725
| Number of Panels/String | 0 | [6 empty] | Percentage of full sun |  |  |  | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15% | 92.15%
| Number of Strings | 0 | [5 empty] | Array 2 | Est Daily KWh production, shading+derating |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | For Peak Sun Hours (PSH) for your location, to go http://www.bom.gov.au/climate/data/
| Spring Max Temp | 21 | DegC |  |  |  |  | Array 1+2 | Est Daily KWh production, Array1+2 |  |  |  | 34.3683 | 31.5759 | 29.1271 | 25.3037 | 21.3352 | 18.3011 | 20.4438 | 25.1318 | 29.5299 | 32.1773 | 32.5425 | 34.2072 | 29.2282
| Winter Min. Temp | 5 | DegC | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Solar Tables lookups |  |  | Get: Daily global solar exposure, in KWH m-2 (Use "mean" for all years)
| String VOC | 0 | V dc |  |  |  |  | KWh/Mon | Current Bill / month |  |  |  | 441.3315 | 402.1812 | 441.3315 | 377.2161 | 389.79 | 402.1556 | 415.5608 | 415.5608 | 389.79 | 377.2161 | 427.095 | 441.3315
| PV Array Max. Volts | 0 |  |  | Voc+y(Tmin-Tstc)M | AS5033-2014 4.2 |  | 425.8333 | Total Daily usage (KWh) |  |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  |  |  | A | 'Solar-tables'!AD212:AE223 | Location-Main
| Array Power | 0 | W |  |  |  |  | 14 | Average Usage during Day (KWh) |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | B | 'Solar-tables'!AD212:AE223 | City1
| String O/Current Protection? | No | Yes/No | 0 | ((Sa-1)xIscmod) > Imodmax ocpr | AS5033-2014 3.3.4 |  | KWh/day | Average Usage during night (KWh) |  |  |  | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 |  |  |  | C | #N/A | City2
| String Fuse Min | 0 | A |  | In > 1.5 x Isc mod | AS5033-2014 3.3.5 |  |  | Daily charge |  |  |  | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998 | 1.9998
| String Fuse Max | 0 | A |  | In < 2.4 x Isc mod | AS5033-2014 3.3.5 |  | 26.74% | FIT rate |  |  |  | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0 | Solar Index
| Fuse Size | 20 | A | MCB 350V min DC rated (Noark) |  |  |  | Night | $ per KWh rate/s DAY |  |  |  | 0.4925 | 0.4925 | 0.4925 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.4925 | 0.4925
| Solar Controller | 0 | # | #N/A |  |  |  | 73.26% | $ per KWh rate/s NIGHT |  |  |  | 0.26685 | 0.26685 | 0.26685 | 0.23138 | 0.23138 | 0.2621 | 0.2621 | 0.2621 | 0.23138 | 0.23138 | 0.26685 | 0.26685 |  | Off Grid?
| Solar Controller Max PV | 7500 | W | (See VE-MPPT Calc Spreadsheet for calcs) |  |  |  | Night | Daily Cost of Power - without system |  |  |  | 14.2365 | 14.2365 | 14.2365 | 12.5739 | 12.5739 | 13.4052 | 13.4052 | 13.4052 | 12.5739 | 12.5739 | 14.2365 | 14.2365 |  | Yes
| Location (from tables) | Sydney |  |  | %age from 1st Location, to second |  |  |  | Daily Cost of Power - with system |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Battery?
| Min PSH for location | 2.4 |  |  | Your Location, PSH data, AF23:AR34 |  |  |  | Daily Feed-in Ret |  | 0 | Ave /mo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
| Shading/Efficiency/Soiling | 95% | [6 empty] | Daily net $ (+pay -paid) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Solar panel roof tilt from 0 | 20 | [6 empty] | Monthly net $ |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | $pay
| Solar aspect (azimuth) | 20 | [6 empty] | Savings |  | 410.0467 | Ave /mo | 441.3315 | 402.1812 | 441.3315 | 377.2161 | 389.79 | 402.1556 | 415.5608 | 415.5608 | 389.79 | 377.2161 | 427.095 | 441.3315 | 4920.56 | $Savings
[9 empty] | Payback period |  | 0 | Years | 0 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56
| Battry Bank Size Selected: | 29.952 | KWh | [5 empty] | NPV of system |  | 59046.7201 | 12 yrs | 0 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56 | 4920.56
Battery | Number of Batteries | 24 |  |  | Per AS2676.2: 1992 |  |  |  | FIT rate |  | 0.115 | Int.rate | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Type | Gel | [6 empty] | total System price: |  | 0 | 0% | 0: Year from Installation >>>>
| Part # | GNB 676Ah Gel | [10 empty] | 0: 30.4167; 1: days/mo
| Module AH (20hr) | 624 | AH |  |  |  |  | w/Batt | Grid Use-night KWh (GR.N) |  |  |  | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806 | 0.79806
| Module Nominal Voltage | 2 | Vdc | [5 empty] | Battery Discharge Night KWh (BD) |  |  |  | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019 | 26.6019
| Strings | 1 | [6 empty] | Battery Recharge Day KWh (BR) |  |  |  | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999 | 28.2999
| Modules/string | 24 | [5 empty] | w/Batt | Grid Use-day KWh (GR.D) |  |  |  | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999 | 38.2999
| Bank Nominal voltage | 48 | Vdc | [5 empty] | Feed-In Day (FI) KWh |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Max. Voltage | 57.6 | Vdc | [5 empty] | Add Grid-use night* |  |  | Total KWh usage | 1: 980; 2: 32.2192; 3: 6.4438; 4: 25.7753; 8: #REF!; 9: $ per KWh rate/s
| Max DOD | 100% | DOD | [5 empty] | Grid use day w/o Batt later |  |  | Daily charge | 1: 1.24; 2: per day; 3: 1.24; 8: #VALUE!; 9: Daily Cost of Power - without system
| Nominal DOD | 80% | DOD | [8 empty] | Rate per KWh | 1: 0.2662; 2: per KWh; 3: 0.2662; 8: #VALUE!; 9: Daily Cost of Power - with system
| Bank Ah Capacity | 624 | Ah | [8 empty] | Seniors discount: | 1: 0.932; 2: per day; 3: 340; 4: per yr; 8: 0; 9: Daily Feed-in Returned
| Module Nominal Capacity | 1.248 | KWh | [8 empty] | Days of Bill | 1: 96; 2: days
| Bank Full Capacity | 29.952 | KWh | [8 empty] | Usage charge | 1: 260.876; 8: Commercial Rates (energy Aus); 12: Batt Effic. | 0.94
| BankUsable Capacity | 29.952 | KWh | C | [7 empty] | Supply charge | 1: 119.0429; 3: 0%; 4: General discount; 9: Peak; 10: 0.5709; 12: C | 0.2
| Nom. Output | 83.3333 | A | 0.13355 | #N/A | [7 empty] | 3: 1.24; 4: Discounted Daily usage rate; 9: Shoulder; 10: 0.3531; 12: CN | 0.03
| Peak. Output | 187.5 | A | 0.30048 | #N/A | [6 empty] | #1 Discount | 3: 1.9998; 4: Commercial Daily usage rate; 9: Off-peak; 10: 0.2189
| Peak. Output | 9000 | W |  | 15sec | [6 empty] | #1 Discount | 3: 0.35; 4: Day Rate KWh (pro rataed)
| Life Cycles | 4000 | Cycles |  | @25degC | [6 empty] | #1 Discount | 3: 0.29; 4: Night Rate KWh (pro rataed); 8: LD; 9: Loads-day; 10: 10; 11: KWh; 12: 7a-5pm
| End of life | 10.9589 | Years | [9 empty] | 3: 0.5709; 4: Peak KWh rate; 8: LN; 9: Loads-night; 10: 27.4; 11: KWh; 12: 5p-7am
| Battery String Fault Current | 4050 | A | 35 | AGM FC Factor | [6 empty] | Total Bill | 1: 379.9189; 3: 0.3531; 4: Shoulder KWh rate; 10: 37.4
| Battery Bank Fault Current | 4050 | A | 35 | AGM FC Factor | [7 empty] | 3: 0.2189; 4: Off-Peak KWh rate
| Min. Cable Size to fuse | #NAME? | mm | [9 empty] | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Target Max Voltage drop | 3 | % | [8 empty] | KWh $ - Day | 0.4925 | 0.4925 | 0.4925 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.42344 | 0.4925 | 0.4925
| Distance of Wire Run | 2 | m | [8 empty] | KWh $ - Night | 0.26685 | 0.26685 | 0.26685 | 0.23138 | 0.23138 | 0.2621 | 0.2621 | 0.2621 | 0.23138 | 0.23138 | 0.26685 | 0.26685
| Peak Supply Current | 195.3125 | A | [9 empty] | Feb: Energy Australia Commercial Rates, 2020; Off-Peak KWh rate Jun: (Pro-rataed, based on set day/nigth hours, see CalcsA sheet)
| Resistance | 0.0014496 | Ohms | [8 empty] | Cost of power no system: | 14.2365 | 14.2365 | 14.2365 | 12.5739 | 12.5739 | 13.4052 | 13.4052 | 13.4052 | 12.5739 | 12.5739 | 14.2365 | 14.2365
| Cable Area | 2.5e-05 | m2
| Voltage Drop-V | 0.28313 | V
| Voltage Drop-% | 0.5899%
| Inverter Size Selected: | 4 | KW
Inverter | Nominal Output | 5000 | VA
| Brand | Victron
| Part # | MultiplusII 48/5000/70 |  |  | See Datasheet | [5 empty] | PVC 90C |  | Feb: Rubber 110C; Mar: Rubber 110C; 0.2189 Apr: PVC 90C
| Nominal Voltage | 48 | V |  | Volts DC | [5 empty] | Current |  | Jan: Wire Size; Feb: Current; Mar: Fault; 0.2189 Apr: Fault; Off-Peak KWh rate May: Auto Size; Off-Peak KWh rate Jun: OD; Off-Peak KWh rate Jul: (* From Chrisensen battery handout)
| Max. Output | 9 | KW |  | Maximum output, usually for short time | [5 empty] | Capacity A | Fault A | Jan: mm2; Feb: Capacity A; Mar: Current; 0.2189 Apr: Current; Off-Peak KWh rate Jul: WW Calculator (Bambach)
| Nominal Output | 4 | KW |  | Nominal output, sustainable over time. | [5 empty] | 54 | 1790 | Jan: 10; Feb: 102; Mar: 1790; 0.2189 Apr: 1460
| Efficiency | 0.96 |  |  | 0.96 = 95% efficient | [5 empty] | 63 | 2327 | Jan: 13; Feb: 63; Mar: 2327; 0.2189 Apr: 1898; Off-Peak KWh rate May: 6B&S
[11 empty] | 72 | 2864 | Jan: 16; Feb: 135; Mar: 2864; 0.2189 Apr: 2336; Off-Peak KWh rate Jul: *current carrying capacity (bundle x 3/conduit)
Energy | Occupancy cycle | 7 | days/wk |  | Per AS4509.2: 2010 | [5 empty] | 85 | 2958 | Jan: 20.26; Feb: 85; Mar: 2958; 0.2189 Apr: 2958; Off-Peak KWh rate May: 4B&S; Off-Peak KWh rate Jun: 8.3mm; Off-Peak KWh rate Jul: http://wirewizard.bambachcables.com.au/
| Estimated usage KWh/day | 15.5 | KWh/day | Nominal power draw | [6 empty] | 97 | 4475 | Jan: 25; Feb: 178; Mar: 4475; 0.2189 Apr: 3650; Off-Peak KWh rate May: 3B&S (26.45mm); Off-Peak KWh rate Jul: 25mm Current carrying cap = 124A, 75DegC single, 151A, 90DegC single
| Estimated usage KWh/day | 15.5 | KWh/day | Winter min | [6 empty] | 119 | 6265 | Jan: 35; Feb: 221; Mar: 6265; 0.2189 Apr: 5110
| Max KW | 3 | KW | Maximum Power draw, instantaneous | [7 empty] | 5774 | Jan: 39.55; Feb: 130; Mar: 5774; 0.2189 Apr: 5774; Off-Peak KWh rate May: 1B&S
| Min Solar - Winter | 2.4 | PSH | Sydney | [6 empty] | 146 | 8950 | Jan: 50; Feb: 279; Mar: 8950; 0.2189 Apr: 7300; Off-Peak KWh rate May: 0B&S (49mm)
| Max Solar - Summer | 6.5 | PSH | Sydney | [6 empty] | 184 | 12530 | Jan: 70; Feb: 351; Mar: 12530; 0.2189 Apr: 10220
| Min Energy Production | 0 | KWh/day | 0.9 | Panel fouling factor | [5 empty] | 230 | 16110 | Jan: 95; Feb: 422; Mar: 16110; 0.2189 Apr: 13870
| Max Energy Production | 0 | KWh/day | 0.9 | Panel fouling factor | [5 empty] | 267 | 21480 | Jan: 120; Feb: 500; Mar: 21480; 0.2189 Apr: 17520
| 3 days Energy Use | 46.5 | KWh | [9 empty] | Mar: (Note Special Design Separation, over 20KA)
|  | 1.9 | Days of 3day Battery capacity needed | [9 empty] | Jan: Gauge Guide
| Estimated usage KWh/day MIN. | 12.3958 | KWh/day | [9 empty] | Jan: Auto Size; Feb: Nom Area mm2; Mar: Nom O.D.mm; 0.2189 Apr: Amp Rating; Off-Peak KWh rate May: Part # Prefix
| 3 days Energy Use min. | 37.1875 | KWh | [9 empty] | Jan: 8 B&S; Feb: 7.71; Mar: 5.5; 0.2189 Apr: 74; Off-Peak KWh rate May: C8
|  | 2.4 | Days of 3day Battery capacity needed | [9 empty] | Jan: 6 B&S; Feb: 13.5; Mar: 7.2; 0.2189 Apr: 103; Off-Peak KWh rate May: C6
[13 empty] | 4 B&S | 20.26 | 8.3 | 135 | C4
[13 empty] | 3 B&S | 26.45 | 10.2 | 168 | C3
[13 empty] | 2 B&S | 32.07 | 11.3 | 188 | C2
[13 empty] | 1 B&S | 39.55 | 12.1 | 210 | C1
[13 empty] | 0 B&S | 49 | 12.7 | 246 | C0
Solar Tables
Generic Solar Table
|  | Location: | Brisbane | Canberra | Darwin | Hobart | Sydney | Melbourne | Adelaide | Alice Springs | Perth | Cairns | Feb: Brisbane; Mar: C234:M269
|  | *Peak sunlight hours = daily solar irradiation | [10 empty] | Feb: Canberra; Mar: C69:M104; Off-Peak KWh rate May: VLOOKUP(L9, INDIRECT("'Solar-tables'!"&VLOOKUP(J13, 'Solar-tables'!R6:S17, 2, FALSE)), (ROUND(L10, 10)/10+2), FALSE)
|  | Source: BOM 2020 | [10 empty] | Feb: Darwin; Mar: C110:M145; Off-Peak KWh rate May: Indirect "formula here"
|  | Month | [10 empty] | Feb: Hobart; Mar: C151:M186; Off-Peak KWh rate May: Brisbane; Off-Peak KWh rate Jun: B-Month; Off-Peak KWh rate Aug: Canberra; Off-Peak KWh rate Nov: Darwin |  | Hobart |  |  | Sydney |  |  | Melbourne |  |  | Adelaide |  |  | Alice Springs |  |  | Perth |  |  | Cairns
|  | January | 6.6 | 7.1 | 5.2 | 6.4 | 6.4 | 6.8 | 7.6 | 7.5 | 8.1 | 5.9 |  | Sydney | C192:M227 |  | Jan | O235:T253 |  | Jan | O276:T294 |  | Jan | O317:T335 |  | Jan | O358:T376 |  | Jan | O399:T417 |  | Jan | O440:T458 |  | Jan | O481:T499 |  | Jan | O522:T540 |  | Jan | O563:T581 |  | Jan | O603:T621
|  | February | 5.9 | 6.1 | 5.4 | 5.1 | 5.6 | 5.9 | 6.8 | 7.1 | 7.1 | 5.6 |  | Melbourne | C233:M268 |  | Feb | V235:AA253 |  | Feb | V276:AA294 |  | Feb | V317:AA335 |  | Feb | V358:AA376 |  | Feb | V399:AA417 |  | Feb | V440:AA458 |  | Feb | V481:AA499 |  | Feb | V522:AA540 |  | Feb | V563:AA581 |  | Feb | V603:AA621
|  | March | 5.2 | 5.1 | 5.9 | 3.6 | 4.8 | 4.6 | 5.4 | 6.6 | 5.8 | 5.3 |  | Adelaide | C274:M309 |  | Mar | AC235:AH253 |  | Mar | AC276:AH294 |  | Mar | AC317:AH335 |  | Mar | AC358:AH376 |  | Mar | AC399:AH417 |  | Mar | AC440:AH458 |  | Mar | AC481:AH499 |  | Mar | AC522:AH540 |  | Mar | AC563:AH581 |  | Mar | AC603:AH621
|  | April | 4.5 | 3.8 | 6.1 | 2.6 | 3.8 | 3.1 | 3.8 | 5.6 | 4.2 | 5 |  | Alice Springs | C315:M350 |  | Apr | AJ235:AO253 |  | Apr | AJ276:AO294 |  | Apr | AJ317:AO335 |  | Apr | AJ358:AO376 |  | Apr | AJ399:AO417 |  | Apr | AJ440:AO458 |  | Apr | AJ481:AO499 |  | Apr | AJ522:AO540 |  | Apr | AJ563:AO581 |  | Apr | AJ603:AO621
|  | May | 3.7 | 2.8 | 5.7 | 1.6 | 2.9 | 2.1 | 2.6 | 4.5 | 3.1 | 4.5 |  | Perth | C356:M391 |  | May | AQ235:AV253 |  | May | AQ276:AV294 |  | May | AQ317:AV335 |  | May | AQ358:AV376 |  | May | AQ399:AV417 |  | May | AQ440:AV458 |  | May | AQ481:AV499 |  | May | AQ522:AV540 |  | May | AQ563:AV581 |  | May | AQ603:AV621
|  | June | 3.3 | 2.2 | 5.5 | 1.3 | 2.4 | 1.7 | 2.2 | 4.1 | 2.6 | 4.2 |  | Cairns | C397:M432 |  | Jun | AX235:BC253 |  | Jun | AX276:BC294 |  | Jun | AX317:BC335 |  | Jun | AX358:BC376 |  | Jun | AX399:BC417 |  | Jun | AX440:BC458 |  | Jun | AX481:BC499 |  | Jun | AX522:BC540 |  | Jun | AX563:BC581 |  | Jun | AX603:BC621
|  | July | 3.6 | 2.5 | 5.7 | 1.5 | 2.7 | 1.9 | 2.4 | 4.4 | 2.8 | 4.5 | Feb: A-Detailed Solar Table, Loc.; Off-Peak KWh rate May: Jul; Off-Peak KWh rate Jun: BE235:BJ253; Off-Peak KWh rate Aug: Jul; Off-Peak KWh rate Sep: BE276:BJ294; Off-Peak KWh rate Nov: Jul; Off-Peak KWh rate Dec: BE317:BJ335 |  | Jul | BE358:BJ376 |  | Jul | BE399:BJ417 |  | Jul | BE440:BJ458 |  | Jul | BE481:BJ499 |  | Jul | BE522:BJ540 |  | Jul | BE563:BJ581 |  | Jul | BE603:BJ621
|  | August | 4.4 | 3.4 | 6.3 | 2.2 | 3.6 | 2.7 | 3.3 | 5.3 | 3.6 | 5.2 |  | Brisbane | R212:S223 |  | Aug | BL235:BQ253 |  | Aug | BL276:BQ294 |  | Aug | BL317:BQ335 |  | Aug | BL358:BQ376 |  | Aug | BL399:BQ417 |  | Aug | BL440:BQ458 |  | Aug | BL481:BQ499 |  | Aug | BL522:BQ540 |  | Aug | BL563:BQ581 |  | Aug | BL603:BQ621
|  | September | 5.4 | 4.6 | 6.6 | 3.3 | 4.7 | 3.7 | 4.4 | 6.2 | 4.7 | 6.1 |  | Canberra | U212:V223 |  | Sep | BS235:BX253 |  | Sep | BS276:BX294 |  | Sep | BS317:BX335 |  | Sep | BS358:BX376 |  | Sep | BS399:BX417 |  | Sep | BS440:BX458 |  | Sep | BS481:BX499 |  | Sep | BS522:BX540 |  | Sep | BS563:BX581 |  | Sep | BS603:BX621
|  | October | 6 | 5.8 | 6.7 | 4.7 | 5.6 | 5 | 5.8 | 7 | 6.3 | 6.5 |  | Darwin | X212:Y223 |  | Oct | BZ235:CE253 |  | Oct | BZ276:CE294 |  | Oct | BZ317:CE335 |  | Oct | BZ358:CE376 |  | Oct | BZ399:CE417 |  | Oct | BZ440:CE458 |  | Oct | BZ481:CE499 |  | Oct | BZ522:CE540 |  | Oct | BZ563:CE581 |  | Oct | BZ603:CE621
|  | November | 6.6 | 6.6 | 6.3 | 5.4 | 6 | 5.9 | 7 | 7.3 | 7.5 | 6.5 |  | Hobart | AA212:AB223 |  | Nov | CG235:CL253 |  | Nov | CG276:CL294 |  | Nov | CG317:CL335 |  | Nov | CG358:CL376 |  | Nov | CG399:CL417 |  | Nov | CG440:CL458 |  | Nov | CG481:CL499 |  | Nov | CG522:CL540 |  | Nov | CG563:CL581 |  | Nov | CG603:CL621
|  | December | 6.7 | 7.2 | 5.6 | 6.3 | 6.5 | 6.7 | 7.5 | 7.4 | 8.3 | 6.3 |  | Sydney | AD212:AE223 |  | Dec | CN235:CS253 |  | Dec | CN276:CS294 |  | Dec | CN317:CS335 |  | Dec | CN358:CS376 |  | Dec | CN399:CS417 |  | Dec | CN440:CS458 |  | Dec | CN481:CS499 |  | Dec | CN522:CS540 |  | Dec | CN563:CS581 |  | Dec | CN603:CS621
|  | Average | 5.2 | 4.8 | 5.9 | 3.7 | 4.6 | 4.2 | 4.9 | 6.1 | 5.3 | 5.5 | Feb: Melbourne; Mar: AG212:AH223
[14 empty] | Adelaide | AJ212:AK223
|  | Total annual solar irradiation* (kWh/m2/year) | 1971 | 1789 | 2117 | 1424 | 1862 | 1679 | 2060 | 2224 | 1935 | 2044 | Feb: Alice Springs; Mar: AM212:AN223
[14 empty] | Perth | AP212:AQ223
|  | CEC GC Design guidelines Issue 5.1 January, 2012 | [10 empty] | Feb: Cairns; Mar: AS212:AT223
ANNUAL DAILY IRRADIATION ON AN INCLINED PLANE EXPRESSED AS % OF MAXIMUM VALUE
|  | 7.1 BRISBANE | [10 empty] | Feb: BRISBANE
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [9 empty] | Feb: BRISBANE - Janurary; Off-Peak KWh rate Sep: BRISBANE - February |  |  |  | BRISBANE - March | [6 empty] | BRISBANE - April | [6 empty] | BRISBANE - May | [5 empty] | BRISBANE - June | [5 empty] | BRISBANE - July | [5 empty] | BRISBANE - August | [5 empty] | BRISBANE - September | [5 empty] | BRISBANE - October | [5 empty] | BRISBANE - November | [5 empty] | BRISBANE - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 90% | 95% | 99% | 100% | 98% | 94% | 88% | 80% | 70% | 59% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 90% | 95% | 99% | 100% | 98% | 94% | 88% | 80% | 71% | 60% |  | 270 | 100% | 100% | 99% | 97% | 92% |  | 270 | 100% | 100% | 99% | 97% | 93% |  | 270 | 100% | 101% | 100% | 97% | 94% |  | 270 | 100% | 100% | 99% | 98% | 94% |  | 270 | 100% | 101% | 101% | 99% | 96% | 270 | 100% | 102% | 101% | 100% | 98% | 270 | 100% | 101% | 101% | 99% | 97% | 270 | 100% | 101% | 100% | 98% | 95% | 270 | 100% | 101% | 100% | 98% | 94% | 270 | 100% | 100% | 100% | 97% | 93% | 270 | 100% | 101% | 99% | 96% | 92% | 270 | 100% | 100% | 99% | 96% | 91%
|  | 20 | 90% | 95% | 98% | 99% | 98% | 94% | 88% | 80% | 71% | 61% |  | 280 | 100% | 100% | 99% | 97% | 92% |  | 280 | 100% | 101% | 100% | 97% | 94% |  | 280 | 100% | 102% | 102% | 100% | 98% |  | 280 | 100% | 102% | 103% | 102% | 101% |  | 280 | 100% | 104% | 106% | 107% | 105% | 280 | 100% | 105% | 107% | 109% | 108% | 280 | 100% | 104% | 106% | 108% | 106% | 280 | 100% | 103% | 105% | 105% | 103% | 280 | 100% | 102% | 103% | 101% | 100% | 280 | 100% | 101% | 101% | 99% | 95% | 280 | 100% | 101% | 100% | 96% | 93% | 280 | 100% | 100% | 98% | 95% | 91%
|  | 30 | 90% | 95% | 98% | 98% | 97% | 93% | 87% | 80% | 71% | 61% |  | 290 | 100% | 100% | 99% | 96% | 92% |  | 290 | 100% | 101% | 100% | 98% | 95% |  | 290 | 100% | 103% | 104% | 103% | 100% |  | 290 | 100% | 104% | 107% | 107% | 107% |  | 290 | 100% | 107% | 111% | 113% | 114% | 290 | 100% | 108% | 113% | 117% | 119% | 290 | 100% | 107% | 113% | 116% | 116% | 290 | 100% | 105% | 109% | 110% | 110% | 290 | 100% | 104% | 105% | 106% | 104% | 290 | 100% | 102% | 102% | 100% | 97% | 290 | 100% | 101% | 100% | 96% | 93% | 290 | 100% | 100% | 98% | 95% | 90%
|  | 40 | 90% | 95% | 97% | 97% | 95% | 92% | 86% | 79% | 71% | 61% |  | 300 | 100% | 100% | 99% | 96% | 91% |  | 300 | 100% | 101% | 101% | 99% | 95% |  | 300 | 100% | 104% | 106% | 105% | 103% |  | 300 | 100% | 106% | 110% | 112% | 112% |  | 300 | 100% | 109% | 116% | 121% | 123% | 300 | 100% | 111% | 120% | 125% | 128% | 300 | 100% | 110% | 118% | 123% | 126% | 300 | 100% | 108% | 113% | 116% | 117% | 300 | 100% | 105% | 108% | 109% | 107% | 300 | 100% | 103% | 103% | 102% | 99% | 300 | 100% | 101% | 100% | 96% | 92% | 300 | 100% | 100% | 98% | 94% | 89%
|  | 50 | 90% | 94% | 96% | 96% | 93% | 90% | 84% | 78% | 70% | 61% |  | 310 | 100% | 100% | 98% | 95% | 90% |  | 310 | 100% | 102% | 101% | 100% | 95% |  | 310 | 100% | 105% | 107% | 107% | 105% |  | 310 | 100% | 108% | 113% | 116% | 117% |  | 310 | 100% | 111% | 121% | 128% | 130% | 310 | 100% | 113% | 124% | 133% | 138% | 310 | 100% | 113% | 123% | 130% | 135% | 310 | 100% | 110% | 117% | 122% | 123% | 310 | 100% | 106% | 110% | 112% | 111% | 310 | 100% | 103% | 104% | 103% | 100% | 310 | 100% | 101% | 99% | 96% | 91% | 310 | 100% | 99% | 97% | 93% | 88%
|  | 60 | 90% | 93% | 94% | 94% | 91% | 88% | 82% | 76% | 69% | 60% |  | 320 | 100% | 100% | 98% | 94% | 89% |  | 320 | 100% | 102% | 102% | 100% | 96% |  | 320 | 100% | 106% | 108% | 109% | 107% |  | 320 | 100% | 109% | 116% | 120% | 121% |  | 320 | 100% | 114% | 125% | 133% | 138% | 320 | 100% | 116% | 129% | 139% | 145% | 320 | 100% | 115% | 128% | 137% | 143% | 320 | 100% | 112% | 120% | 126% | 129% | 320 | 100% | 107% | 112% | 114% | 113% | 320 | 100% | 103% | 105% | 103% | 100% | 320 | 100% | 101% | 99% | 96% | 91% | 320 | 100% | 99% | 97% | 92% | 86%
|  | 70 | 90% | 92% | 93% | 92% | 89% | 85% | 80% | 74% | 67% | 59% |  | 330 | 100% | 100% | 98% | 93% | 87% |  | 330 | 100% | 102% | 102% | 100% | 95% |  | 330 | 100% | 106% | 109% | 110% | 109% |  | 330 | 100% | 110% | 118% | 123% | 125% |  | 330 | 100% | 115% | 128% | 138% | 143% | 330 | 100% | 118% | 133% | 145% | 152% | 330 | 100% | 117% | 131% | 142% | 149% | 330 | 100% | 113% | 123% | 130% | 134% | 330 | 100% | 108% | 113% | 116% | 116% | 330 | 100% | 103% | 105% | 104% | 100% | 330 | 100% | 101% | 99% | 95% | 89% | 330 | 100% | 99% | 96% | 91% | 84%
|  | 80 | 90% | 91% | 91% | 89% | 86% | 82% | 77% | 71% | 64% | 57% |  | 340 | 100% | 100% | 97% | 93% | 86% |  | 340 | 100% | 102% | 102% | 100% | 95% |  | 340 | 100% | 107% | 110% | 112% | 110% |  | 340 | 100% | 111% | 120% | 125% | 128% |  | 340 | 100% | 117% | 131% | 141% | 148% | 340 | 100% | 120% | 136% | 148% | 158% | 340 | 100% | 118% | 134% | 146% | 154% | 340 | 100% | 114% | 125% | 133% | 137% | 340 | 100% | 108% | 114% | 118% | 118% | 340 | 100% | 104% | 105% | 104% | 100% | 340 | 100% | 100% | 99% | 95% | 89% | 340 | 100% | 99% | 95% | 90% | 83%
|  | 90 | 90% | 91% | 89% | 87% | 83% | 79% | 74% | 68% | 61% | 55% |  | 350 | 100% | 100% | 97% | 92% | 85% |  | 350 | 100% | 102% | 102% | 100% | 95% |  | 350 | 100% | 107% | 111% | 112% | 111% |  | 350 | 100% | 112% | 121% | 127% | 130% |  | 350 | 100% | 117% | 132% | 144% | 151% | 350 | 100% | 120% | 138% | 151% | 161% | 350 | 100% | 119% | 135% | 148% | 157% | 350 | 100% | 114% | 126% | 135% | 139% | 350 | 100% | 109% | 115% | 118% | 119% | 350 | 100% | 104% | 105% | 104% | 100% | 350 | 100% | 100% | 98% | 94% | 88% | 350 | 100% | 99% | 95% | 90% | 83%
|  | 100 | 90% | 90% | 88% | 84% | 80% | 75% | 70% | 64% | 58% | 52% |  | 0 | 100% | 99% | 97% | 92% | 85% |  | 0 | 100% | 102% | 102% | 99% | 95% |  | 0 | 100% | 107% | 111% | 112% | 111% |  | 0 | 100% | 112% | 121% | 128% | 130% |  | 0 | 100% | 118% | 133% | 144% | 152% | 0 | 100% | 120% | 138% | 152% | 162% | 0 | 100% | 119% | 136% | 149% | 158% | 0 | 100% | 114% | 127% | 135% | 140% | 0 | 100% | 109% | 115% | 119% | 119% | 0 | 100% | 104% | 105% | 104% | 100% | 0 | 100% | 100% | 98% | 94% | 88% | 0 | 100% | 99% | 95% | 90% | 82%
|  | 110 | 90% | 89% | 86% | 82% | 77% | 71% | 65% | 60% | 54% | 48% |  | 10 | 100% | 99% | 97% | 92% | 85% |  | 10 | 100% | 102% | 102% | 100% | 95% |  | 10 | 100% | 107% | 111% | 112% | 110% |  | 10 | 100% | 112% | 121% | 127% | 130% |  | 10 | 100% | 117% | 132% | 143% | 151% | 10 | 100% | 120% | 138% | 151% | 161% | 10 | 100% | 119% | 135% | 148% | 157% | 10 | 100% | 114% | 126% | 135% | 139% | 10 | 100% | 109% | 115% | 118% | 118% | 10 | 100% | 104% | 105% | 103% | 100% | 10 | 100% | 100% | 98% | 94% | 88% | 10 | 100% | 99% | 95% | 90% | 82%
|  | 120 | 90% | 88% | 84% | 79% | 73% | 67% | 61% | 55% | 50% | 44% |  | 20 | 100% | 99% | 97% | 92% | 85% |  | 20 | 100% | 102% | 102% | 100% | 95% |  | 20 | 100% | 107% | 110% | 111% | 109% |  | 20 | 100% | 111% | 120% | 125% | 128% |  | 20 | 100% | 117% | 131% | 141% | 148% | 20 | 100% | 120% | 136% | 148% | 157% | 20 | 100% | 118% | 134% | 145% | 154% | 20 | 100% | 114% | 125% | 133% | 137% | 20 | 100% | 108% | 114% | 117% | 117% | 20 | 100% | 103% | 105% | 103% | 100% | 20 | 100% | 100% | 98% | 94% | 88% | 20 | 100% | 99% | 96% | 90% | 83%
|  | 130 | 90% | 87% | 82% | 76% | 70% | 63% | 57% | 51% | 45% | 40% |  | 30 | 100% | 99% | 97% | 92% | 86% |  | 30 | 100% | 102% | 102% | 99% | 95% |  | 30 | 100% | 106% | 109% | 110% | 108% |  | 30 | 100% | 110% | 118% | 123% | 125% |  | 30 | 100% | 115% | 128% | 138% | 143% | 30 | 100% | 118% | 133% | 144% | 152% | 30 | 100% | 117% | 131% | 142% | 148% | 30 | 100% | 113% | 123% | 129% | 134% | 30 | 100% | 107% | 113% | 115% | 115% | 30 | 100% | 103% | 104% | 103% | 99% | 30 | 100% | 100% | 98% | 95% | 89% | 30 | 100% | 99% | 96% | 91% | 84%
|  | 140 | 90% | 86% | 81% | 74% | 66% | 59% | 52% | 46% | 41% | 36% |  | 40 | 100% | 99% | 97% | 93% | 87% |  | 40 | 100% | 102% | 101% | 99% | 95% |  | 40 | 100% | 106% | 108% | 109% | 107% |  | 40 | 100% | 109% | 116% | 120% | 121% |  | 40 | 100% | 114% | 125% | 133% | 137% | 40 | 100% | 116% | 129% | 138% | 145% | 40 | 100% | 115% | 127% | 136% | 142% | 40 | 100% | 112% | 120% | 126% | 129% | 40 | 100% | 107% | 111% | 113% | 112% | 40 | 100% | 103% | 103% | 102% | 98% | 40 | 100% | 100% | 98% | 95% | 89% | 40 | 100% | 99% | 96% | 92% | 86%
|  | 150 | 90% | 86% | 80% | 72% | 64% | 56% | 48% | 42% | 37% | 32% |  | 50 | 100% | 99% | 97% | 93% | 88% |  | 50 | 100% | 101% | 101% | 99% | 95% |  | 50 | 100% | 105% | 107% | 107% | 105% |  | 50 | 100% | 108% | 113% | 117% | 117% |  | 50 | 100% | 111% | 121% | 127% | 130% | 50 | 100% | 113% | 124% | 132% | 137% | 50 | 100% | 113% | 123% | 130% | 134% | 50 | 100% | 109% | 117% | 121% | 123% | 50 | 100% | 106% | 109% | 110% | 109% | 50 | 100% | 102% | 103% | 101% | 97% | 50 | 100% | 100% | 98% | 95% | 90% | 50 | 100% | 99% | 97% | 93% | 87%
|  | 160 | 90% | 85% | 79% | 71% | 61% | 53% | 45% | 39% | 34% | 30% |  | 60 | 100% | 100% | 97% | 94% | 89% |  | 60 | 100% | 101% | 100% | 98% | 95% |  | 60 | 100% | 104% | 105% | 105% | 103% |  | 60 | 100% | 106% | 111% | 112% | 113% |  | 60 | 100% | 109% | 116% | 121% | 123% | 60 | 100% | 111% | 119% | 124% | 127% | 60 | 100% | 110% | 118% | 123% | 126% | 60 | 100% | 108% | 113% | 116% | 117% | 60 | 100% | 104% | 107% | 107% | 106% | 60 | 100% | 102% | 102% | 100% | 96% | 60 | 100% | 100% | 98% | 95% | 91% | 60 | 100% | 100% | 97% | 93% | 88%
|  | 170 | 90% | 85% | 78% | 69% | 60% | 51% | 44% | 37% | 31% | 28% |  | 70 | 100% | 100% | 98% | 94% | 90% |  | 70 | 100% | 101% | 100% | 98% | 94% |  | 70 | 100% | 103% | 104% | 102% | 100% |  | 70 | 100% | 104% | 107% | 108% | 107% |  | 70 | 100% | 107% | 111% | 114% | 114% | 70 | 100% | 108% | 113% | 116% | 117% | 70 | 100% | 107% | 112% | 116% | 116% | 70 | 100% | 105% | 109% | 110% | 110% | 70 | 100% | 103% | 104% | 104% | 101% | 70 | 100% | 101% | 100% | 98% | 95% | 70 | 100% | 100% | 98% | 95% | 91% | 70 | 100% | 100% | 98% | 94% | 90%
|  | 180 | 90% | 85% | 78% | 69% | 59% | 51% | 43% | 36% | 30% | 27% |  | 80 | 100% | 100% | 98% | 94% | 90% |  | 80 | 100% | 100% | 99% | 97% | 93% |  | 80 | 100% | 101% | 101% | 100% | 97% |  | 80 | 100% | 103% | 103% | 103% | 101% |  | 80 | 100% | 104% | 106% | 107% | 105% | 80 | 100% | 105% | 107% | 108% | 108% | 80 | 100% | 104% | 106% | 107% | 106% | 80 | 100% | 103% | 104% | 105% | 103% | 80 | 100% | 101% | 101% | 100% | 97% | 80 | 100% | 100% | 99% | 97% | 92% | 80 | 100% | 100% | 98% | 95% | 91% | 80 | 100% | 100% | 98% | 95% | 90%
|  | 190 | 90% | 85% | 78% | 69% | 59% | 51% | 43% | 37% | 31% | 27% |  | 90 | 100% | 100% | 98% | 95% | 90% |  | 90 | 100% | 100% | 98% | 96% | 92% |  | 90 | 100% | 100% | 100% | 97% | 93% |  | 90 | 100% | 101% | 99% | 98% | 96% |  | 90 | 100% | 101% | 101% | 99% | 97% | 90 | 100% | 101% | 101% | 99% | 98% | 90 | 100% | 101% | 101% | 99% | 97% | 90 | 100% | 101% | 99% | 98% | 95% | 90 | 100% | 100% | 99% | 96% | 93% | 90 | 100% | 100% | 98% | 95% | 90% | 90 | 100% | 100% | 98% | 95% | 91% | 90 | 100% | 100% | 98% | 95% | 91%
|  | 200 | 90% | 85% | 78% | 70% | 60% | 52% | 45% | 38% | 32% | 29%
|  | 210 | 90% | 85% | 79% | 71% | 62% | 54% | 47% | 41% | 36% | 31%
|  | 220 | 90% | 86% | 80% | 73% | 65% | 57% | 51% | 45% | 39% | 35%
|  | 230 | 90% | 86% | 81% | 75% | 68% | 61% | 55% | 49% | 43% | 38%
|  | 240 | 90% | 87% | 83% | 77% | 71% | 65% | 59% | 53% | 48% | 42%
|  | 250 | 90% | 88% | 84% | 80% | 74% | 69% | 63% | 57% | 52% | 46%
|  | 260 | 90% | 89% | 86% | 82% | 78% | 73% | 67% | 61% | 55% | 49%
|  | 270 | 90% | 90% | 88% | 85% | 81% | 76% | 71% | 65% | 59% | 52%
|  | 280 | 90% | 91% | 90% | 87% | 84% | 79% | 74% | 68% | 61% | 55%
|  | 290 | 90% | 92% | 91% | 90% | 86% | 82% | 77% | 71% | 64% | 56%
|  | 300 | 90% | 92% | 93% | 92% | 89% | 85% | 79% | 73% | 66% | 58%
|  | 310 | 90% | 93% | 94% | 94% | 91% | 87% | 82% | 75% | 67% | 59%
|  | 320 | 90% | 94% | 96% | 96% | 93% | 89% | 84% | 77% | 69% | 59%
|  | 330 | 90% | 95% | 97% | 97% | 95% | 91% | 85% | 78% | 69% | 60%
|  | 340 | 90% | 95% | 98% | 98% | 97% | 93% | 87% | 79% | 70% | 60%
|  | 350 | 90% | 95% | 98% | 99% | 98% | 94% | 88% | 80% | 70% | 59%
|  | 7.2 CANBERRA | [11 empty] | CANBERRA
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | CANBERRA - Janurary | [6 empty] | CANBERRA - February | [6 empty] | CANBERRA - March | [6 empty] | CANBERRA - April | [6 empty] | CANBERRA - May | [5 empty] | CANBERRA - June | [5 empty] | CANBERRA - July | [5 empty] | CANBERRA - August | [5 empty] | CANBERRA - September | [5 empty] | CANBERRA - October | [5 empty] | CANBERRA - November | [5 empty] | CANBERRA - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 87% | 94% | 98% | 100% | 99% | 96% | 91% | 83% | 74% | 64% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 87% | 94% | 98% | 99% | 99% | 96% | 91% | 83% | 74% | 64% |  | 270 | 100% | 100% | 99% | 96% | 93% |  | 270 | 100% | 100% | 99% | 97% | 93% |  | 270 | 100% | 101% | 101% | 99% | 96% |  | 270 | 100% | 101% | 101% | 100% | 98% |  | 270 | 100% | 101% | 102% | 101% | 100% | 270 | 100% | 101% | 103% | 103% | 102% | 270 | 100% | 102% | 103% | 103% | 102% | 270 | 100% | 101% | 101% | 100% | 99% | 270 | 100% | 101% | 101% | 99% | 96% | 270 | 100% | 101% | 100% | 98% | 95% | 270 | 100% | 100% | 99% | 97% | 93% | 270 | 100% | 100% | 99% | 96% | 92%
|  | 20 | 87% | 93% | 97% | 99% | 98% | 95% | 90% | 83% | 74% | 64% |  | 280 | 100% | 101% | 100% | 97% | 93% |  | 280 | 100% | 101% | 101% | 99% | 96% |  | 280 | 100% | 103% | 104% | 103% | 101% |  | 280 | 100% | 103% | 105% | 107% | 105% |  | 280 | 100% | 105% | 108% | 110% | 111% | 280 | 100% | 105% | 111% | 113% | 115% | 280 | 100% | 106% | 110% | 112% | 114% | 280 | 100% | 104% | 107% | 108% | 108% | 280 | 100% | 103% | 104% | 104% | 102% | 280 | 100% | 102% | 102% | 101% | 98% | 280 | 100% | 101% | 100% | 98% | 94% | 280 | 100% | 100% | 99% | 96% | 93%
|  | 30 | 87% | 93% | 96% | 98% | 97% | 94% | 89% | 82% | 73% | 64% |  | 290 | 100% | 101% | 100% | 98% | 94% |  | 290 | 100% | 102% | 102% | 100% | 98% |  | 290 | 100% | 104% | 107% | 107% | 106% |  | 290 | 100% | 106% | 110% | 112% | 113% |  | 290 | 100% | 108% | 115% | 120% | 122% | 290 | 100% | 110% | 118% | 123% | 127% | 290 | 100% | 110% | 117% | 123% | 126% | 290 | 100% | 107% | 113% | 116% | 117% | 290 | 100% | 105% | 108% | 108% | 108% | 290 | 100% | 103% | 104% | 103% | 101% | 290 | 100% | 101% | 101% | 98% | 95% | 290 | 100% | 101% | 99% | 97% | 93%
|  | 40 | 87% | 92% | 95% | 96% | 95% | 92% | 87% | 80% | 72% | 63% |  | 300 | 100% | 101% | 100% | 98% | 94% |  | 300 | 100% | 103% | 103% | 102% | 100% |  | 300 | 100% | 105% | 109% | 110% | 110% |  | 300 | 100% | 108% | 114% | 118% | 120% |  | 300 | 100% | 112% | 121% | 129% | 133% | 300 | 100% | 114% | 124% | 133% | 139% | 300 | 100% | 113% | 124% | 132% | 137% | 300 | 100% | 110% | 118% | 123% | 126% | 300 | 100% | 107% | 111% | 113% | 113% | 300 | 100% | 104% | 105% | 105% | 103% | 300 | 100% | 102% | 101% | 99% | 96% | 300 | 100% | 101% | 99% | 96% | 92%
|  | 50 | 87% | 92% | 94% | 94% | 93% | 89% | 84% | 78% | 70% | 62% |  | 310 | 100% | 101% | 101% | 98% | 94% |  | 310 | 100% | 103% | 104% | 103% | 100% |  | 310 | 100% | 107% | 111% | 113% | 113% |  | 310 | 100% | 110% | 118% | 124% | 126% |  | 310 | 100% | 115% | 127% | 136% | 142% | 310 | 100% | 117% | 131% | 143% | 150% | 310 | 100% | 116% | 130% | 141% | 148% | 310 | 100% | 113% | 122% | 129% | 133% | 310 | 100% | 108% | 114% | 117% | 117% | 310 | 100% | 104% | 107% | 107% | 105% | 310 | 100% | 102% | 102% | 99% | 96% | 310 | 100% | 101% | 99% | 96% | 92%
|  | 60 | 87% | 91% | 92% | 92% | 90% | 86% | 81% | 75% | 68% | 61% |  | 320 | 100% | 101% | 101% | 98% | 93% |  | 320 | 100% | 103% | 105% | 104% | 101% |  | 320 | 100% | 108% | 113% | 115% | 115% |  | 320 | 100% | 112% | 122% | 128% | 132% |  | 320 | 100% | 118% | 132% | 144% | 152% | 320 | 100% | 119% | 137% | 150% | 161% | 320 | 100% | 119% | 135% | 149% | 157% | 320 | 100% | 114% | 126% | 135% | 140% | 320 | 100% | 109% | 116% | 120% | 121% | 320 | 100% | 105% | 108% | 108% | 106% | 320 | 100% | 102% | 102% | 100% | 96% | 320 | 100% | 101% | 99% | 96% | 91%
|  | 70 | 87% | 90% | 90% | 89% | 87% | 83% | 78% | 72% | 66% | 59% |  | 330 | 100% | 101% | 101% | 97% | 93% |  | 330 | 100% | 104% | 105% | 105% | 102% |  | 330 | 100% | 108% | 114% | 117% | 118% |  | 330 | 100% | 114% | 124% | 132% | 137% |  | 330 | 100% | 119% | 136% | 150% | 159% | 330 | 100% | 122% | 141% | 157% | 169% | 330 | 100% | 121% | 140% | 154% | 166% | 330 | 100% | 116% | 129% | 139% | 146% | 330 | 100% | 110% | 118% | 122% | 124% | 330 | 100% | 105% | 109% | 109% | 107% | 330 | 100% | 102% | 102% | 100% | 95% | 330 | 100% | 101% | 99% | 95% | 90%
|  | 80 | 87% | 89% | 88% | 87% | 84% | 80% | 75% | 69% | 63% | 56% |  | 340 | 100% | 101% | 101% | 97% | 92% |  | 340 | 100% | 104% | 106% | 105% | 102% |  | 340 | 100% | 109% | 115% | 118% | 119% |  | 340 | 100% | 114% | 126% | 135% | 140% |  | 340 | 100% | 121% | 140% | 154% | 165% | 340 | 100% | 123% | 145% | 162% | 176% | 340 | 100% | 123% | 143% | 159% | 171% | 340 | 100% | 118% | 132% | 143% | 150% | 340 | 100% | 111% | 120% | 125% | 127% | 340 | 100% | 106% | 109% | 110% | 108% | 340 | 100% | 102% | 102% | 100% | 95% | 340 | 100% | 100% | 99% | 95% | 89%
|  | 90 | 87% | 88% | 86% | 84% | 80% | 76% | 71% | 65% | 59% | 53% |  | 350 | 100% | 101% | 100% | 97% | 92% |  | 350 | 100% | 104% | 106% | 105% | 102% |  | 350 | 100% | 109% | 116% | 119% | 120% |  | 350 | 100% | 115% | 127% | 137% | 142% |  | 350 | 100% | 122% | 142% | 157% | 169% | 350 | 100% | 124% | 147% | 165% | 179% | 350 | 100% | 124% | 145% | 162% | 175% | 350 | 100% | 118% | 133% | 145% | 153% | 350 | 100% | 112% | 121% | 126% | 129% | 350 | 100% | 106% | 109% | 110% | 108% | 350 | 100% | 102% | 102% | 99% | 95% | 350 | 100% | 100% | 99% | 95% | 89%
|  | 100 | 87% | 87% | 84% | 81% | 77% | 72% | 67% | 61% | 56% | 50% |  | 0 | 100% | 101% | 100% | 97% | 92% |  | 0 | 100% | 104% | 106% | 105% | 102% |  | 0 | 100% | 109% | 116% | 119% | 120% |  | 0 | 100% | 115% | 128% | 137% | 143% |  | 0 | 100% | 122% | 142% | 158% | 169% | 0 | 100% | 126% | 147% | 166% | 180% | 0 | 100% | 124% | 146% | 163% | 176% | 0 | 100% | 118% | 134% | 146% | 154% | 0 | 100% | 112% | 121% | 127% | 129% | 0 | 100% | 106% | 110% | 110% | 108% | 0 | 100% | 102% | 102% | 99% | 94% | 0 | 100% | 100% | 99% | 94% | 88%
|  | 110 | 87% | 86% | 82% | 78% | 73% | 68% | 62% | 57% | 51% | 46% |  | 10 | 100% | 101% | 100% | 97% | 92% |  | 10 | 100% | 104% | 106% | 105% | 102% |  | 10 | 100% | 109% | 115% | 119% | 119% |  | 10 | 100% | 115% | 127% | 137% | 142% |  | 10 | 100% | 122% | 142% | 157% | 168% | 10 | 100% | 124% | 147% | 165% | 179% | 10 | 100% | 124% | 145% | 161% | 174% | 10 | 100% | 118% | 133% | 145% | 153% | 10 | 100% | 112% | 121% | 126% | 129% | 10 | 100% | 106% | 109% | 110% | 108% | 10 | 100% | 102% | 102% | 100% | 95% | 10 | 100% | 100% | 99% | 95% | 89%
|  | 120 | 87% | 85% | 80% | 75% | 69% | 63% | 58% | 52% | 47% | 42% |  | 20 | 100% | 101% | 100% | 97% | 92% |  | 20 | 100% | 104% | 105% | 105% | 102% |  | 20 | 100% | 109% | 114% | 118% | 118% |  | 20 | 100% | 114% | 126% | 135% | 140% |  | 20 | 100% | 121% | 139% | 153% | 164% | 20 | 100% | 123% | 144% | 161% | 174% | 20 | 100% | 123% | 142% | 158% | 170% | 20 | 100% | 117% | 132% | 143% | 150% | 20 | 100% | 111% | 120% | 125% | 127% | 20 | 100% | 105% | 109% | 109% | 107% | 20 | 100% | 102% | 102% | 100% | 95% | 20 | 100% | 100% | 99% | 95% | 89%
|  | 130 | 87% | 84% | 78% | 72% | 66% | 59% | 53% | 48% | 43% | 38% |  | 30 | 100% | 101% | 100% | 97% | 92% |  | 30 | 100% | 104% | 105% | 105% | 102% |  | 30 | 100% | 108% | 113% | 116% | 116% |  | 30 | 100% | 113% | 124% | 131% | 136% |  | 30 | 100% | 119% | 136% | 149% | 158% | 30 | 100% | 121% | 140% | 155% | 167% | 30 | 100% | 121% | 138% | 153% | 163% | 30 | 100% | 116% | 129% | 138% | 145% | 30 | 100% | 110% | 118% | 123% | 124% | 30 | 100% | 105% | 108% | 108% | 106% | 30 | 100% | 102% | 102% | 100% | 96% | 30 | 100% | 100% | 99% | 95% | 90%
|  | 140 | 87% | 83% | 77% | 70% | 62% | 55% | 49% | 44% | 39% | 35% |  | 40 | 100% | 101% | 100% | 97% | 93% |  | 40 | 100% | 103% | 105% | 104% | 101% |  | 40 | 100% | 107% | 112% | 114% | 114% |  | 40 | 100% | 112% | 121% | 128% | 131% |  | 40 | 100% | 117% | 131% | 143% | 151% | 40 | 100% | 119% | 135% | 149% | 159% | 40 | 100% | 118% | 134% | 146% | 155% | 40 | 100% | 114% | 126% | 134% | 139% | 40 | 100% | 109% | 116% | 120% | 122% | 40 | 100% | 105% | 107% | 107% | 105% | 40 | 100% | 102% | 102% | 100% | 96% | 40 | 100% | 100% | 99% | 95% | 90%
|  | 150 | 87% | 82% | 76% | 68% | 60% | 52% | 45% | 40% | 35% | 32% |  | 50 | 100% | 101% | 100% | 97% | 93% |  | 50 | 100% | 103% | 104% | 103% | 100% |  | 50 | 100% | 106% | 110% | 111% | 111% |  | 50 | 100% | 110% | 118% | 124% | 125% |  | 50 | 100% | 114% | 126% | 136% | 142% | 50 | 100% | 116% | 130% | 140% | 148% | 50 | 100% | 115% | 129% | 138% | 145% | 50 | 100% | 112% | 121% | 129% | 132% | 50 | 100% | 108% | 114% | 117% | 117% | 50 | 100% | 104% | 105% | 106% | 104% | 50 | 100% | 102% | 102% | 100% | 96% | 50 | 100% | 100% | 99% | 96% | 91%
|  | 160 | 87% | 82% | 75% | 66% | 57% | 50% | 42% | 36% | 33% | 29% |  | 60 | 100% | 101% | 100% | 97% | 93% |  | 60 | 100% | 102% | 103% | 102% | 99% |  | 60 | 100% | 105% | 107% | 108% | 107% |  | 60 | 100% | 108% | 114% | 118% | 120% |  | 60 | 100% | 112% | 120% | 128% | 132% | 60 | 100% | 113% | 123% | 131% | 136% | 60 | 100% | 112% | 122% | 130% | 134% | 60 | 100% | 110% | 117% | 122% | 125% | 60 | 100% | 107% | 111% | 113% | 113% | 60 | 100% | 103% | 105% | 104% | 102% | 60 | 100% | 102% | 101% | 99% | 96% | 60 | 100% | 100% | 99% | 96% | 91%
|  | 170 | 87% | 82% | 74% | 65% | 56% | 48% | 41% | 35% | 30% | 28% |  | 70 | 100% | 101% | 100% | 97% | 93% |  | 70 | 100% | 102% | 102% | 100% | 97% |  | 70 | 100% | 103% | 105% | 105% | 104% |  | 70 | 100% | 106% | 110% | 112% | 113% |  | 70 | 100% | 108% | 114% | 119% | 121% | 70 | 100% | 109% | 116% | 121% | 124% | 70 | 100% | 109% | 115% | 120% | 123% | 70 | 100% | 107% | 112% | 115% | 116% | 70 | 100% | 104% | 108% | 109% | 108% | 70 | 100% | 102% | 103% | 102% | 100% | 70 | 100% | 101% | 100% | 98% | 95% | 70 | 100% | 100% | 99% | 96% | 91%
|  | 180 | 87% | 81% | 74% | 65% | 56% | 48% | 40% | 34% | 30% | 27% |  | 80 | 100% | 100% | 99% | 96% | 92% |  | 80 | 100% | 101% | 100% | 99% | 95% |  | 80 | 100% | 102% | 102% | 101% | 99% |  | 80 | 100% | 103% | 105% | 106% | 105% |  | 80 | 100% | 104% | 108% | 110% | 110% | 80 | 100% | 105% | 109% | 111% | 113% | 80 | 100% | 105% | 108% | 110% | 110% | 80 | 100% | 104% | 107% | 108% | 107% | 80 | 100% | 103% | 104% | 104% | 102% | 80 | 100% | 101% | 101% | 100% | 97% | 80 | 100% | 101% | 100% | 98% | 94% | 80 | 100% | 100% | 99% | 96% | 91%
|  | 190 | 87% | 81% | 74% | 65% | 56% | 48% | 41% | 35% | 30% | 28% |  | 90 | 100% | 100% | 99% | 96% | 91% |  | 90 | 100% | 100% | 99% | 97% | 93% |  | 90 | 100% | 100% | 99% | 97% | 94% |  | 90 | 100% | 101% | 101% | 99% | 98% |  | 90 | 100% | 101% | 101% | 100% | 99% | 90 | 100% | 101% | 101% | 101% | 100% | 90 | 100% | 101% | 101% | 100% | 99% | 90 | 100% | 101% | 101% | 100% | 99% | 90 | 100% | 101% | 101% | 99% | 96% | 90 | 100% | 100% | 99% | 97% | 93% | 90 | 100% | 100% | 99% | 96% | 93% | 90 | 100% | 100% | 98% | 95% | 91%
|  | 200 | 87% | 82% | 74% | 66% | 57% | 50% | 42% | 36% | 32% | 29%
|  | 210 | 87% | 82% | 75% | 67% | 59% | 52% | 45% | 40% | 35% | 32%
|  | 220 | 87% | 83% | 77% | 69% | 62% | 55% | 49% | 43% | 39% | 35%
|  | 230 | 87% | 84% | 78% | 72% | 65% | 59% | 53% | 48% | 43% | 38%
|  | 240 | 87% | 84% | 80% | 74% | 68% | 63% | 57% | 52% | 47% | 41%
|  | 250 | 87% | 85% | 82% | 77% | 72% | 67% | 62% | 56% | 51% | 45%
|  | 260 | 87% | 86% | 84% | 80% | 76% | 71% | 66% | 61% | 55% | 49%
|  | 270 | 87% | 87% | 86% | 83% | 79% | 75% | 70% | 65% | 59% | 52%
|  | 280 | 87% | 89% | 88% | 86% | 83% | 79% | 74% | 68% | 62% | 55%
|  | 290 | 87% | 90% | 90% | 89% | 86% | 82% | 77% | 71% | 65% | 58%
|  | 300 | 87% | 91% | 92% | 91% | 89% | 85% | 81% | 74% | 67% | 60%
|  | 310 | 87% | 91% | 93% | 94% | 92% | 88% | 83% | 77% | 70% | 61%
|  | 320 | 87% | 92% | 95% | 96% | 94% | 91% | 86% | 79% | 71% | 63%
|  | 330 | 87% | 93% | 96% | 97% | 96% | 93% | 88% | 81% | 73% | 63%
|  | 340 | 87% | 93% | 97% | 98% | 98% | 95% | 89% | 82% | 74% | 64%
|  | 350 | 87% | 94% | 98% | 99% | 99% | 95% | 90% | 83% | 74% | 64%
|  | 7.3 DARWIN | [11 empty] | DARWIN
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | DARWIN - Janurary | [6 empty] | DARWIN - February | [6 empty] | DARWIN - March | [6 empty] | DARWIN - April | [6 empty] | DARWIN - May | [5 empty] | DARWIN - June | [5 empty] | DARWIN - July | [5 empty] | DARWIN - August | [5 empty] | DARWIN - September | [5 empty] | DARWIN - October | [5 empty] | DARWIN - November | [5 empty] | DARWIN - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 96% | 99% | 100% | 99% | 94% | 88% | 79% | 69% | 58% | 48% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 96% | 99% | 100% | 99% | 94% | 88% | 79% | 69% | 58% | 48% |  | 270 | 100% | 100% | 97% | 94% | 89% |  | 270 | 100% | 100% | 98% | 94% | 90% |  | 270 | 100% | 100% | 98% | 94% | 90% |  | 270 | 100% | 100% | 99% | 96% | 92% |  | 270 | 100% | 100% | 100% | 97% | 93% | 270 | 100% | 100% | 100% | 97% | 93% | 270 | 100% | 100% | 100% | 97% | 93% | 270 | 100% | 100% | 99% | 97% | 93% | 270 | 100% | 101% | 100% | 97% | 93% | 270 | 100% | 100% | 99% | 96% | 92% | 270 | 100% | 100% | 98% | 95% | 90% | 270 | 100% | 100% | 97% | 94% | 89%
|  | 20 | 96% | 99% | 100% | 98% | 94% | 88% | 80% | 70% | 59% | 49% |  | 280 | 100% | 99% | 96% | 92% | 87% |  | 280 | 100% | 100% | 97% | 93% | 89% |  | 280 | 100% | 100% | 99% | 96% | 92% |  | 280 | 100% | 101% | 101% | 99% | 96% |  | 280 | 100% | 103% | 103% | 102% | 99% | 280 | 100% | 103% | 104% | 102% | 100% | 280 | 100% | 103% | 104% | 102% | 100% | 280 | 100% | 102% | 102% | 100% | 98% | 280 | 100% | 102% | 101% | 99% | 96% | 280 | 100% | 100% | 99% | 96% | 92% | 280 | 100% | 100% | 98% | 93% | 89% | 280 | 100% | 99% | 96% | 92% | 87%
|  | 30 | 96% | 99% | 100% | 98% | 94% | 88% | 80% | 71% | 61% | 51% |  | 290 | 100% | 98% | 95% | 90% | 85% |  | 290 | 100% | 100% | 97% | 93% | 88% |  | 290 | 100% | 100% | 100% | 97% | 93% |  | 290 | 100% | 103% | 103% | 102% | 99% |  | 290 | 100% | 105% | 107% | 107% | 105% | 290 | 100% | 105% | 108% | 108% | 107% | 290 | 100% | 105% | 108% | 108% | 107% | 290 | 100% | 103% | 105% | 104% | 102% | 290 | 100% | 102% | 102% | 101% | 97% | 290 | 100% | 100% | 99% | 96% | 91% | 290 | 100% | 99% | 96% | 92% | 87% | 290 | 100% | 98% | 95% | 90% | 85%
|  | 40 | 96% | 99% | 99% | 97% | 93% | 88% | 80% | 71% | 62% | 53% |  | 300 | 100% | 98% | 94% | 89% | 83% |  | 300 | 100% | 100% | 97% | 92% | 87% |  | 300 | 100% | 101% | 100% | 98% | 93% |  | 300 | 100% | 104% | 105% | 105% | 102% |  | 300 | 100% | 106% | 110% | 111% | 110% | 300 | 100% | 107% | 111% | 114% | 113% | 300 | 100% | 107% | 111% | 113% | 112% | 300 | 100% | 105% | 107% | 108% | 106% | 300 | 100% | 103% | 103% | 102% | 98% | 300 | 100% | 100% | 99% | 96% | 91% | 300 | 100% | 99% | 96% | 91% | 85% | 300 | 100% | 98% | 93% | 89% | 82%
|  | 50 | 96% | 98% | 99% | 96% | 93% | 87% | 80% | 72% | 63% | 55% |  | 310 | 100% | 97% | 93% | 87% | 81% |  | 310 | 100% | 99% | 96% | 92% | 86% |  | 310 | 100% | 101% | 100% | 98% | 94% |  | 310 | 100% | 105% | 107% | 107% | 105% |  | 310 | 100% | 108% | 113% | 115% | 115% | 310 | 100% | 109% | 115% | 119% | 120% | 310 | 100% | 109% | 115% | 118% | 118% | 310 | 100% | 106% | 109% | 111% | 109% | 310 | 100% | 104% | 104% | 103% | 100% | 310 | 100% | 100% | 99% | 95% | 90% | 310 | 100% | 98% | 94% | 89% | 83% | 310 | 100% | 97% | 92% | 87% | 79%
|  | 60 | 96% | 98% | 98% | 96% | 92% | 86% | 80% | 72% | 64% | 56% |  | 320 | 100% | 97% | 92% | 86% | 79% |  | 320 | 100% | 99% | 96% | 91% | 84% |  | 320 | 100% | 101% | 101% | 99% | 94% |  | 320 | 100% | 106% | 109% | 109% | 107% |  | 320 | 100% | 109% | 115% | 119% | 119% | 320 | 100% | 110% | 118% | 123% | 125% | 320 | 100% | 110% | 118% | 122% | 123% | 320 | 100% | 107% | 112% | 113% | 113% | 320 | 100% | 104% | 105% | 104% | 100% | 320 | 100% | 100% | 98% | 95% | 89% | 320 | 100% | 98% | 93% | 87% | 80% | 320 | 100% | 96% | 91% | 85% | 77%
|  | 70 | 96% | 97% | 97% | 94% | 91% | 85% | 79% | 72% | 64% | 56% |  | 330 | 100% | 97% | 92% | 85% | 77% |  | 330 | 100% | 99% | 96% | 91% | 84% |  | 330 | 100% | 102% | 101% | 99% | 94% |  | 330 | 100% | 106% | 110% | 111% | 109% |  | 330 | 100% | 110% | 118% | 122% | 123% | 330 | 100% | 112% | 121% | 127% | 130% | 330 | 100% | 111% | 120% | 125% | 127% | 330 | 100% | 108% | 113% | 116% | 115% | 330 | 100% | 104% | 106% | 105% | 101% | 330 | 100% | 100% | 98% | 94% | 88% | 330 | 100% | 98% | 93% | 86% | 78% | 330 | 100% | 96% | 90% | 83% | 75%
|  | 80 | 96% | 97% | 96% | 93% | 89% | 84% | 78% | 71% | 63% | 56% |  | 340 | 100% | 97% | 91% | 84% | 76% |  | 340 | 100% | 99% | 96% | 90% | 83% |  | 340 | 100% | 102% | 102% | 100% | 94% |  | 340 | 100% | 107% | 111% | 112% | 111% |  | 340 | 100% | 111% | 119% | 124% | 126% | 340 | 100% | 113% | 123% | 130% | 133% | 340 | 100% | 112% | 122% | 128% | 131% | 340 | 100% | 109% | 114% | 117% | 117% | 340 | 100% | 104% | 106% | 105% | 102% | 340 | 100% | 100% | 98% | 93% | 87% | 340 | 100% | 97% | 92% | 85% | 76% | 340 | 100% | 96% | 90% | 82% | 74%
|  | 90 | 96% | 96% | 95% | 92% | 87% | 82% | 76% | 69% | 62% | 55% |  | 350 | 100% | 97% | 91% | 83% | 75% |  | 350 | 100% | 99% | 96% | 90% | 82% |  | 350 | 100% | 102% | 102% | 100% | 95% |  | 350 | 100% | 107% | 112% | 113% | 112% |  | 350 | 100% | 112% | 120% | 126% | 128% | 350 | 100% | 113% | 124% | 132% | 136% | 350 | 100% | 113% | 123% | 129% | 133% | 350 | 100% | 109% | 115% | 119% | 119% | 350 | 100% | 104% | 106% | 105% | 102% | 350 | 100% | 100% | 98% | 93% | 86% | 350 | 100% | 97% | 92% | 85% | 76% | 350 | 100% | 96% | 89% | 82% | 72%
|  | 100 | 96% | 96% | 93% | 90% | 85% | 79% | 73% | 67% | 59% | 52% |  | 0 | 100% | 97% | 91% | 84% | 75% |  | 0 | 100% | 99% | 96% | 90% | 83% |  | 0 | 100% | 102% | 102% | 100% | 95% |  | 0 | 100% | 108% | 112% | 114% | 112% |  | 0 | 100% | 112% | 121% | 126% | 128% | 0 | 100% | 114% | 125% | 132% | 136% | 0 | 100% | 113% | 123% | 130% | 133% | 0 | 100% | 109% | 115% | 119% | 119% | 0 | 100% | 104% | 106% | 105% | 102% | 0 | 100% | 100% | 98% | 93% | 86% | 0 | 100% | 97% | 92% | 84% | 75% | 0 | 100% | 96% | 89% | 82% | 72%
|  | 110 | 96% | 95% | 93% | 88% | 83% | 77% | 70% | 63% | 56% | 49% |  | 10 | 100% | 97% | 91% | 84% | 76% |  | 10 | 100% | 99% | 96% | 91% | 83% |  | 10 | 100% | 102% | 103% | 100% | 95% |  | 10 | 100% | 107% | 112% | 113% | 112% |  | 10 | 100% | 112% | 120% | 125% | 128% | 10 | 100% | 113% | 124% | 131% | 135% | 10 | 100% | 113% | 123% | 129% | 132% | 10 | 100% | 109% | 115% | 118% | 118% | 10 | 100% | 104% | 106% | 105% | 101% | 10 | 100% | 100% | 98% | 93% | 86% | 10 | 100% | 97% | 92% | 85% | 76% | 10 | 100% | 96% | 90% | 82% | 73%
|  | 120 | 96% | 94% | 91% | 86% | 80% | 74% | 67% | 59% | 52% | 46% |  | 20 | 100% | 97% | 92% | 85% | 77% |  | 20 | 100% | 100% | 97% | 91% | 85% |  | 20 | 100% | 102% | 103% | 100% | 96% |  | 20 | 100% | 107% | 111% | 112% | 111% |  | 20 | 100% | 111% | 119% | 124% | 126% | 20 | 100% | 113% | 123% | 130% | 133% | 20 | 100% | 112% | 121% | 127% | 130% | 20 | 100% | 108% | 114% | 117% | 116% | 20 | 100% | 104% | 106% | 104% | 100% | 20 | 100% | 100% | 97% | 93% | 86% | 20 | 100% | 98% | 92% | 85% | 77% | 20 | 100% | 96% | 90% | 83% | 75%
|  | 130 | 96% | 94% | 90% | 84% | 78% | 70% | 63% | 56% | 48% | 41% |  | 30 | 100% | 98% | 93% | 87% | 79% |  | 30 | 100% | 100% | 97% | 92% | 86% |  | 30 | 100% | 102% | 102% | 100% | 96% |  | 30 | 100% | 106% | 110% | 111% | 109% |  | 30 | 100% | 110% | 117% | 122% | 123% | 30 | 100% | 112% | 121% | 127% | 129% | 30 | 100% | 111% | 119% | 125% | 126% | 30 | 100% | 108% | 113% | 115% | 114% | 30 | 100% | 104% | 105% | 103% | 100% | 30 | 100% | 100% | 98% | 93% | 86% | 30 | 100% | 98% | 93% | 87% | 79% | 30 | 100% | 97% | 91% | 85% | 77%
|  | 140 | 96% | 93% | 89% | 82% | 75% | 67% | 59% | 51% | 44% | 37% |  | 40 | 100% | 98% | 94% | 89% | 82% |  | 40 | 100% | 100% | 98% | 93% | 88% |  | 40 | 100% | 102% | 102% | 100% | 96% |  | 40 | 100% | 106% | 109% | 110% | 108% |  | 40 | 100% | 109% | 115% | 119% | 119% | 40 | 100% | 110% | 118% | 123% | 124% | 40 | 100% | 110% | 117% | 121% | 122% | 40 | 100% | 106% | 111% | 112% | 111% | 40 | 100% | 103% | 104% | 102% | 98% | 40 | 100% | 100% | 98% | 93% | 88% | 40 | 100% | 98% | 94% | 88% | 81% | 40 | 100% | 97% | 93% | 87% | 79%
|  | 150 | 96% | 93% | 88% | 81% | 73% | 64% | 55% | 46% | 39% | 33% |  | 50 | 100% | 99% | 95% | 91% | 84% |  | 50 | 100% | 100% | 98% | 95% | 89% |  | 50 | 100% | 102% | 102% | 100% | 96% |  | 50 | 100% | 105% | 108% | 108% | 105% |  | 50 | 100% | 108% | 113% | 115% | 114% | 50 | 100% | 109% | 115% | 118% | 119% | 50 | 100% | 109% | 114% | 117% | 117% | 50 | 100% | 106% | 109% | 109% | 107% | 50 | 100% | 103% | 103% | 101% | 97% | 50 | 100% | 100% | 98% | 93% | 88% | 50 | 100% | 98% | 95% | 89% | 83% | 50 | 100% | 98% | 94% | 89% | 82%
|  | 160 | 96% | 93% | 87% | 80% | 71% | 61% | 51% | 43% | 36% | 30% |  | 60 | 100% | 99% | 97% | 92% | 87% |  | 60 | 100% | 100% | 99% | 96% | 91% |  | 60 | 100% | 102% | 101% | 100% | 96% |  | 60 | 100% | 104% | 106% | 105% | 103% |  | 60 | 100% | 106% | 110% | 110% | 109% | 60 | 100% | 107% | 111% | 113% | 113% | 60 | 100% | 107% | 110% | 112% | 111% | 60 | 100% | 104% | 106% | 106% | 104% | 60 | 100% | 102% | 102% | 99% | 96% | 60 | 100% | 100% | 98% | 94% | 89% | 60 | 100% | 99% | 96% | 91% | 85% | 60 | 100% | 99% | 95% | 91% | 85%
|  | 170 | 96% | 93% | 87% | 79% | 70% | 59% | 49% | 41% | 34% | 28% |  | 70 | 100% | 100% | 98% | 94% | 89% |  | 70 | 100% | 101% | 100% | 97% | 92% |  | 70 | 100% | 101% | 101% | 99% | 95% |  | 70 | 100% | 103% | 104% | 103% | 100% |  | 70 | 100% | 104% | 106% | 106% | 104% | 70 | 100% | 105% | 107% | 107% | 106% | 70 | 100% | 104% | 107% | 107% | 105% | 70 | 100% | 103% | 104% | 103% | 100% | 70 | 100% | 101% | 101% | 98% | 94% | 70 | 100% | 100% | 98% | 94% | 89% | 70 | 100% | 100% | 97% | 93% | 87% | 70 | 100% | 99% | 97% | 93% | 88%
|  | 180 | 96% | 92% | 86% | 78% | 69% | 58% | 48% | 40% | 33% | 27% |  | 80 | 100% | 100% | 99% | 96% | 92% |  | 80 | 100% | 101% | 100% | 97% | 93% |  | 80 | 100% | 101% | 100% | 98% | 94% |  | 80 | 100% | 102% | 102% | 100% | 96% |  | 80 | 100% | 102% | 103% | 101% | 98% | 80 | 100% | 102% | 103% | 102% | 99% | 80 | 100% | 102% | 103% | 101% | 99% | 80 | 100% | 101% | 101% | 99% | 95% | 80 | 100% | 100% | 99% | 96% | 92% | 80 | 100% | 100% | 98% | 95% | 89% | 80 | 100% | 100% | 98% | 94% | 89% | 80 | 100% | 100% | 98% | 95% | 90%
|  | 190 | 96% | 92% | 86% | 78% | 69% | 59% | 48% | 41% | 33% | 27% |  | 90 | 100% | 101% | 100% | 98% | 94% |  | 90 | 100% | 101% | 100% | 98% | 94% |  | 90 | 100% | 100% | 100% | 97% | 93% |  | 90 | 100% | 100% | 99% | 96% | 92% |  | 90 | 100% | 100% | 99% | 96% | 92% | 90 | 100% | 100% | 99% | 96% | 92% | 90 | 100% | 100% | 99% | 96% | 91% | 90 | 100% | 100% | 98% | 95% | 91% | 90 | 100% | 100% | 98% | 94% | 90% | 90 | 100% | 100% | 98% | 95% | 89% | 90 | 100% | 100% | 99% | 96% | 91% | 90 | 100% | 100% | 100% | 97% | 93%
|  | 200 | 96% | 93% | 87% | 79% | 70% | 60% | 50% | 42% | 35% | 29%
|  | 210 | 96% | 93% | 87% | 80% | 71% | 63% | 53% | 45% | 38% | 32%
|  | 220 | 96% | 93% | 88% | 81% | 74% | 65% | 57% | 49% | 42% | 36%
|  | 230 | 96% | 93% | 89% | 83% | 76% | 68% | 60% | 53% | 46% | 40%
|  | 240 | 96% | 94% | 90% | 85% | 78% | 71% | 64% | 57% | 50% | 44%
|  | 250 | 96% | 94% | 91% | 86% | 81% | 74% | 67% | 61% | 54% | 47%
|  | 260 | 96% | 95% | 92% | 88% | 83% | 77% | 70% | 64% | 57% | 50%
|  | 270 | 96% | 96% | 93% | 90% | 85% | 79% | 73% | 67% | 60% | 52%
|  | 280 | 96% | 96% | 95% | 91% | 87% | 81% | 75% | 68% | 61% | 54%
|  | 290 | 96% | 97% | 96% | 93% | 89% | 83% | 77% | 70% | 62% | 55%
|  | 300 | 96% | 97% | 96% | 94% | 90% | 84% | 78% | 70% | 63% | 55%
|  | 310 | 96% | 98% | 97% | 95% | 91% | 85% | 78% | 70% | 62% | 54%
|  | 320 | 96% | 98% | 98% | 96% | 92% | 86% | 78% | 70% | 61% | 52%
|  | 330 | 96% | 99% | 99% | 97% | 93% | 86% | 78% | 70% | 60% | 51%
|  | 340 | 96% | 99% | 100% | 98% | 93% | 87% | 79% | 69% | 59% | 49%
|  | 350 | 96% | 99% | 100% | 98% | 94% | 87% | 79% | 69% | 58% | 48%
|  | 7.4 HOBART | [11 empty] | HOBART
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | HOBART - Janurary | [6 empty] | HOBART - February | [6 empty] | HOBART - March | [6 empty] | HOBART - April | [6 empty] | HOBART - May | [5 empty] | HOBART - June | [5 empty] | HOBART - July | [5 empty] | HOBART - August | [5 empty] | HOBART - September | [5 empty] | HOBART - October | [5 empty] | HOBART - November | [5 empty] | HOBART - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 82% | 90% | 95% | 99% | 100% | 99% | 95% | 89% | 81% | 72% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 82% | 89% | 95% | 98% | 99% | 98% | 95% | 88% | 81% | 72% |  | 270 | 100% | 101% | 100% | 98% | 94% |  | 270 | 100% | 101% | 101% | 100% | 97% |  | 270 | 100% | 101% | 100% | 99% | 98% |  | 270 | 100% | 101% | 102% | 101% | 100% |  | 270 | 100% | 101% | 103% | 104% | 103% | 270 | 100% | 102% | 103% | 103% | 103% | 270 | 100% | 101% | 103% | 104% | 104% | 270 | 100% | 101% | 101% | 101% | 100% | 270 | 100% | 101% | 101% | 100% | 98% | 270 | 100% | 101% | 101% | 99% | 96% | 270 | 100% | 101% | 100% | 99% | 96% | 270 | 100% | 101% | 100% | 97% | 94%
|  | 20 | 82% | 89% | 95% | 98% | 99% | 97% | 94% | 88% | 81% | 72% |  | 280 | 100% | 101% | 101% | 99% | 96% |  | 280 | 100% | 102% | 103% | 102% | 100% |  | 280 | 100% | 102% | 104% | 104% | 102% |  | 280 | 100% | 104% | 106% | 108% | 109% |  | 280 | 100% | 105% | 110% | 113% | 115% | 280 | 100% | 106% | 111% | 116% | 117% | 280 | 100% | 107% | 111% | 115% | 117% | 280 | 100% | 104% | 108% | 109% | 110% | 280 | 100% | 103% | 105% | 105% | 105% | 280 | 100% | 102% | 103% | 102% | 101% | 280 | 100% | 102% | 102% | 100% | 97% | 280 | 100% | 101% | 100% | 98% | 95%
|  | 30 | 82% | 88% | 93% | 96% | 97% | 96% | 92% | 87% | 79% | 70% |  | 290 | 100% | 102% | 102% | 100% | 98% |  | 290 | 100% | 103% | 105% | 104% | 103% |  | 290 | 100% | 104% | 107% | 108% | 107% |  | 290 | 100% | 106% | 112% | 115% | 116% |  | 290 | 100% | 109% | 117% | 123% | 127% | 290 | 100% | 111% | 120% | 128% | 133% | 290 | 100% | 111% | 119% | 126% | 132% | 290 | 100% | 107% | 113% | 117% | 120% | 290 | 100% | 105% | 109% | 111% | 111% | 290 | 100% | 104% | 105% | 105% | 104% | 290 | 100% | 102% | 103% | 102% | 99% | 290 | 100% | 101% | 101% | 99% | 96%
|  | 40 | 82% | 88% | 92% | 95% | 95% | 93% | 90% | 84% | 78% | 69% |  | 300 | 100% | 102% | 103% | 102% | 98% |  | 300 | 100% | 104% | 106% | 106% | 105% |  | 300 | 100% | 106% | 110% | 112% | 112% |  | 300 | 100% | 109% | 116% | 121% | 124% |  | 300 | 100% | 113% | 124% | 132% | 138% | 300 | 100% | 116% | 130% | 141% | 147% | 300 | 100% | 115% | 128% | 138% | 144% | 300 | 100% | 110% | 119% | 125% | 129% | 300 | 100% | 108% | 113% | 116% | 117% | 300 | 100% | 105% | 107% | 108% | 107% | 300 | 100% | 103% | 103% | 103% | 100% | 300 | 100% | 102% | 101% | 100% | 96%
|  | 50 | 82% | 87% | 90% | 92% | 92% | 90% | 87% | 81% | 75% | 67% |  | 310 | 100% | 102% | 103% | 102% | 99% |  | 310 | 100% | 105% | 107% | 108% | 107% |  | 310 | 100% | 107% | 112% | 115% | 116% |  | 310 | 100% | 111% | 121% | 127% | 131% |  | 310 | 100% | 115% | 129% | 141% | 149% | 310 | 100% | 120% | 138% | 152% | 163% | 310 | 100% | 119% | 135% | 149% | 158% | 310 | 100% | 113% | 124% | 132% | 138% | 310 | 100% | 109% | 116% | 121% | 123% | 310 | 100% | 106% | 109% | 110% | 109% | 310 | 100% | 103% | 104% | 103% | 101% | 310 | 100% | 102% | 102% | 100% | 96%
|  | 60 | 82% | 86% | 88% | 90% | 89% | 87% | 83% | 78% | 72% | 65% |  | 320 | 100% | 103% | 104% | 102% | 99% |  | 320 | 100% | 105% | 108% | 109% | 108% |  | 320 | 100% | 109% | 115% | 118% | 119% |  | 320 | 100% | 113% | 124% | 132% | 138% |  | 320 | 100% | 119% | 136% | 149% | 159% | 320 | 100% | 123% | 144% | 161% | 175% | 320 | 100% | 122% | 142% | 158% | 169% | 320 | 100% | 116% | 128% | 138% | 145% | 320 | 100% | 111% | 118% | 124% | 127% | 320 | 100% | 106% | 110% | 112% | 111% | 320 | 100% | 103% | 105% | 104% | 101% | 320 | 100% | 102% | 102% | 100% | 96%
|  | 70 | 82% | 85% | 87% | 87% | 85% | 83% | 79% | 75% | 69% | 62% |  | 330 | 100% | 103% | 104% | 102% | 99% |  | 330 | 100% | 106% | 109% | 110% | 109% |  | 330 | 100% | 109% | 116% | 121% | 122% |  | 330 | 100% | 114% | 127% | 137% | 143% |  | 330 | 100% | 121% | 140% | 155% | 167% | 330 | 100% | 127% | 150% | 170% | 186% | 330 | 100% | 125% | 147% | 165% | 179% | 330 | 100% | 117% | 132% | 144% | 153% | 330 | 100% | 112% | 121% | 127% | 131% | 330 | 100% | 107% | 111% | 113% | 113% | 330 | 100% | 103% | 105% | 104% | 101% | 330 | 100% | 102% | 102% | 100% | 96%
|  | 80 | 82% | 84% | 84% | 84% | 82% | 79% | 75% | 70% | 65% | 59% |  | 340 | 100% | 103% | 104% | 102% | 98% |  | 340 | 100% | 106% | 109% | 110% | 109% |  | 340 | 100% | 110% | 118% | 122% | 125% |  | 340 | 100% | 116% | 129% | 139% | 146% |  | 340 | 100% | 123% | 144% | 160% | 173% | 340 | 100% | 128% | 155% | 177% | 194% | 340 | 100% | 128% | 151% | 171% | 188% | 340 | 100% | 119% | 135% | 148% | 158% | 340 | 100% | 113% | 123% | 129% | 134% | 340 | 100% | 107% | 112% | 114% | 114% | 340 | 100% | 103% | 105% | 104% | 101% | 340 | 100% | 102% | 102% | 100% | 95%
|  | 90 | 82% | 82% | 82% | 80% | 78% | 75% | 71% | 66% | 61% | 55% |  | 350 | 100% | 103% | 104% | 102% | 98% |  | 350 | 100% | 106% | 109% | 110% | 109% |  | 350 | 100% | 110% | 118% | 123% | 126% |  | 350 | 100% | 117% | 130% | 142% | 149% |  | 350 | 100% | 124% | 145% | 163% | 177% | 350 | 100% | 130% | 156% | 180% | 198% | 350 | 100% | 128% | 154% | 175% | 192% | 350 | 100% | 120% | 137% | 152% | 162% | 350 | 100% | 113% | 124% | 131% | 136% | 350 | 100% | 108% | 112% | 115% | 114% | 350 | 100% | 103% | 105% | 104% | 101% | 350 | 100% | 102% | 102% | 99% | 95%
|  | 100 | 82% | 81% | 79% | 76% | 73% | 70% | 66% | 61% | 56% | 52% |  | 0 | 100% | 103% | 104% | 102% | 98% |  | 0 | 100% | 106% | 109% | 110% | 109% |  | 0 | 100% | 111% | 119% | 124% | 126% |  | 0 | 100% | 117% | 131% | 143% | 150% |  | 0 | 100% | 124% | 146% | 164% | 178% | 0 | 100% | 130% | 158% | 181% | 200% | 0 | 100% | 129% | 154% | 176% | 193% | 0 | 100% | 120% | 137% | 153% | 163% | 0 | 100% | 114% | 124% | 132% | 136% | 0 | 100% | 108% | 112% | 115% | 114% | 0 | 100% | 103% | 105% | 104% | 100% | 0 | 100% | 102% | 102% | 99% | 94%
|  | 110 | 82% | 80% | 77% | 73% | 69% | 65% | 61% | 56% | 52% | 47% |  | 10 | 100% | 103% | 104% | 102% | 98% |  | 10 | 100% | 106% | 109% | 109% | 108% |  | 10 | 100% | 110% | 118% | 124% | 126% |  | 10 | 100% | 117% | 130% | 142% | 149% |  | 10 | 100% | 123% | 145% | 163% | 177% | 10 | 100% | 130% | 156% | 180% | 198% | 10 | 100% | 128% | 154% | 175% | 192% | 10 | 100% | 120% | 137% | 152% | 162% | 10 | 100% | 113% | 124% | 131% | 136% | 10 | 100% | 108% | 112% | 114% | 114% | 10 | 100% | 103% | 105% | 103% | 100% | 10 | 100% | 102% | 102% | 99% | 95%
|  | 120 | 82% | 79% | 75% | 70% | 65% | 60% | 56% | 52% | 47% | 42% |  | 20 | 100% | 103% | 103% | 101% | 98% |  | 20 | 100% | 105% | 108% | 109% | 107% |  | 20 | 100% | 110% | 118% | 123% | 125% |  | 20 | 100% | 116% | 129% | 139% | 146% |  | 20 | 100% | 123% | 142% | 160% | 173% | 20 | 100% | 128% | 155% | 177% | 194% | 20 | 100% | 128% | 151% | 171% | 188% | 20 | 100% | 119% | 135% | 148% | 159% | 20 | 100% | 113% | 123% | 129% | 134% | 20 | 100% | 107% | 112% | 114% | 113% | 20 | 100% | 103% | 104% | 103% | 100% | 20 | 100% | 102% | 102% | 99% | 95%
|  | 130 | 82% | 78% | 72% | 66% | 61% | 55% | 51% | 47% | 42% | 38% |  | 30 | 100% | 102% | 103% | 101% | 98% |  | 30 | 100% | 105% | 107% | 108% | 106% |  | 30 | 100% | 109% | 117% | 121% | 123% |  | 30 | 100% | 114% | 127% | 137% | 143% |  | 30 | 100% | 121% | 140% | 155% | 167% | 30 | 100% | 127% | 150% | 170% | 186% | 30 | 100% | 125% | 147% | 165% | 179% | 30 | 100% | 118% | 133% | 144% | 154% | 30 | 100% | 112% | 121% | 127% | 131% | 30 | 100% | 107% | 111% | 113% | 112% | 30 | 100% | 103% | 104% | 103% | 100% | 30 | 100% | 102% | 102% | 99% | 95%
|  | 140 | 82% | 76% | 70% | 64% | 57% | 51% | 46% | 42% | 38% | 35% |  | 40 | 100% | 102% | 102% | 101% | 97% |  | 40 | 100% | 104% | 106% | 107% | 105% |  | 40 | 100% | 109% | 115% | 118% | 120% |  | 40 | 100% | 113% | 124% | 132% | 138% |  | 40 | 100% | 118% | 135% | 147% | 158% | 40 | 100% | 123% | 144% | 163% | 175% | 40 | 100% | 122% | 142% | 158% | 169% | 40 | 100% | 116% | 129% | 140% | 147% | 40 | 100% | 111% | 118% | 124% | 127% | 40 | 100% | 106% | 110% | 111% | 111% | 40 | 100% | 103% | 103% | 102% | 99% | 40 | 100% | 102% | 101% | 99% | 95%
|  | 150 | 82% | 76% | 68% | 61% | 54% | 47% | 42% | 38% | 35% | 32% |  | 50 | 100% | 102% | 102% | 100% | 97% |  | 50 | 100% | 103% | 105% | 105% | 103% |  | 50 | 100% | 107% | 113% | 116% | 117% |  | 50 | 100% | 111% | 121% | 127% | 131% |  | 50 | 100% | 115% | 129% | 140% | 147% | 50 | 100% | 120% | 138% | 152% | 163% | 50 | 100% | 119% | 135% | 149% | 158% | 50 | 100% | 113% | 125% | 133% | 139% | 50 | 100% | 109% | 116% | 121% | 122% | 50 | 100% | 105% | 108% | 109% | 108% | 50 | 100% | 102% | 103% | 101% | 98% | 50 | 100% | 102% | 101% | 99% | 96%
|  | 160 | 82% | 75% | 67% | 59% | 52% | 45% | 39% | 35% | 32% | 29% |  | 60 | 100% | 101% | 101% | 99% | 96% |  | 60 | 100% | 103% | 104% | 103% | 101% |  | 60 | 100% | 106% | 110% | 112% | 113% |  | 60 | 100% | 109% | 116% | 121% | 124% |  | 60 | 100% | 113% | 123% | 131% | 137% | 60 | 100% | 116% | 130% | 141% | 148% | 60 | 100% | 115% | 128% | 138% | 146% | 60 | 100% | 111% | 120% | 126% | 131% | 60 | 100% | 108% | 113% | 116% | 117% | 60 | 100% | 104% | 106% | 107% | 106% | 60 | 100% | 102% | 102% | 100% | 97% | 60 | 100% | 101% | 101% | 98% | 95%
|  | 170 | 82% | 75% | 67% | 58% | 50% | 43% | 37% | 32% | 30% | 28% |  | 70 | 100% | 101% | 100% | 98% | 94% |  | 70 | 100% | 102% | 102% | 101% | 99% |  | 70 | 100% | 104% | 107% | 109% | 109% |  | 70 | 100% | 106% | 112% | 115% | 117% |  | 70 | 100% | 109% | 117% | 122% | 126% | 70 | 100% | 111% | 122% | 130% | 134% | 70 | 100% | 111% | 119% | 126% | 131% | 70 | 100% | 108% | 114% | 119% | 122% | 70 | 100% | 105% | 109% | 111% | 112% | 70 | 100% | 103% | 105% | 105% | 103% | 70 | 100% | 101% | 100% | 99% | 96% | 70 | 100% | 101% | 100% | 98% | 94%
|  | 180 | 82% | 75% | 66% | 58% | 50% | 43% | 36% | 32% | 29% | 27% |  | 80 | 100% | 100% | 99% | 97% | 93% |  | 80 | 100% | 101% | 100% | 99% | 96% |  | 80 | 100% | 103% | 104% | 104% | 104% |  | 80 | 100% | 104% | 106% | 108% | 109% |  | 80 | 100% | 105% | 109% | 112% | 114% | 80 | 100% | 106% | 113% | 117% | 120% | 80 | 100% | 107% | 113% | 115% | 118% | 80 | 100% | 105% | 109% | 111% | 112% | 80 | 100% | 103% | 105% | 105% | 105% | 80 | 100% | 102% | 102% | 102% | 99% | 80 | 100% | 100% | 100% | 97% | 94% | 80 | 100% | 101% | 100% | 97% | 93%
|  | 190 | 82% | 75% | 67% | 58% | 50% | 43% | 37% | 33% | 30% | 28% |  | 90 | 100% | 100% | 98% | 95% | 91% |  | 90 | 100% | 100% | 98% | 96% | 92% |  | 90 | 100% | 101% | 101% | 100% | 98% |  | 90 | 100% | 101% | 101% | 101% | 101% |  | 90 | 100% | 100% | 101% | 103% | 101% | 90 | 100% | 102% | 103% | 105% | 105% | 90 | 100% | 101% | 103% | 104% | 104% | 90 | 100% | 102% | 103% | 103% | 103% | 90 | 100% | 101% | 101% | 100% | 99% | 90 | 100% | 101% | 100% | 98% | 95% | 90 | 100% | 100% | 98% | 96% | 92% | 90 | 100% | 100% | 99% | 96% | 92%
|  | 200 | 82% | 75% | 67% | 59% | 52% | 45% | 39% | 35% | 32% | 29%
|  | 210 | 82% | 76% | 68% | 61% | 54% | 47% | 42% | 38% | 35% | 32%
|  | 220 | 82% | 76% | 70% | 63% | 56% | 51% | 46% | 42% | 38% | 35%
|  | 230 | 82% | 77% | 72% | 66% | 60% | 55% | 51% | 47% | 42% | 38%
|  | 240 | 82% | 78% | 74% | 69% | 64% | 60% | 56% | 52% | 47% | 42%
|  | 250 | 82% | 79% | 76% | 73% | 68% | 65% | 61% | 56% | 52% | 46%
|  | 260 | 82% | 81% | 79% | 76% | 73% | 69% | 65% | 61% | 56% | 50%
|  | 270 | 82% | 82% | 81% | 79% | 77% | 74% | 70% | 65% | 61% | 55%
|  | 280 | 82% | 83% | 84% | 83% | 81% | 78% | 75% | 70% | 64% | 58%
|  | 290 | 82% | 85% | 86% | 86% | 85% | 82% | 79% | 74% | 68% | 61%
|  | 300 | 82% | 85% | 88% | 89% | 88% | 86% | 82% | 78% | 72% | 64%
|  | 310 | 82% | 87% | 90% | 92% | 92% | 90% | 86% | 81% | 74% | 67%
|  | 320 | 82% | 88% | 92% | 94% | 95% | 93% | 89% | 84% | 76% | 68%
|  | 330 | 82% | 88% | 93% | 96% | 96% | 95% | 92% | 86% | 79% | 70%
|  | 340 | 82% | 89% | 95% | 98% | 98% | 97% | 93% | 87% | 80% | 71%
|  | 350 | 82% | 89% | 95% | 98% | 99% | 98% | 95% | 88% | 81% | 72%
|  | 7.5 SYDNEY | [11 empty] | Sydney
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | Sydney - Janurary | [6 empty] | Sydney - February | [6 empty] | Sydney - March | [6 empty] | Sydney - April | [6 empty] | Sydney - May | [5 empty] | Sydney - June | [5 empty] | Sydney - July | [5 empty] | Sydney - August | [5 empty] | Sydney - September | [5 empty] | Sydney - October | [5 empty] | Sydney - November | [5 empty] | Sydney - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 87% | 94% | 98% | 100% | 99% | 97% | 91% | 84% | 75% | 64% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 87% | 94% | 98% | 100% | 99% | 96% | 91% | 84% | 75% | 64% |  | 270 | 100% | 100% | 99% | 96% | 92% |  | 270 | 100% | 101% | 100% | 97% | 94% |  | 270 | 100% | 101% | 101% | 99% | 96% |  | 270 | 100% | 101% | 101% | 99% | 97% |  | 270 | 100% | 102% | 102% | 101% | 99% | 270 | 100% | 101% | 101% | 101% | 100% | 270 | 100% | 101% | 102% | 101% | 100% | 270 | 100% | 101% | 101% | 99% | 97% | 270 | 100% | 101% | 101% | 99% | 96% | 270 | 100% | 100% | 100% | 98% | 95% | 270 | 100% | 101% | 100% | 97% | 94% | 270 | 100% | 101% | 100% | 97% | 93%
|  | 20 | 87% | 93% | 97% | 99% | 98% | 95% | 90% | 83% | 74% | 64% |  | 280 | 100% | 100% | 99% | 97% | 93% |  | 280 | 100% | 101% | 101% | 99% | 96% |  | 280 | 100% | 103% | 103% | 103% | 101% |  | 280 | 100% | 103% | 105% | 105% | 104% |  | 280 | 100% | 105% | 108% | 110% | 109% | 280 | 100% | 105% | 109% | 111% | 111% | 280 | 100% | 105% | 109% | 111% | 111% | 280 | 100% | 103% | 106% | 107% | 106% | 280 | 100% | 103% | 104% | 103% | 102% | 280 | 100% | 101% | 102% | 100% | 98% | 280 | 100% | 101% | 100% | 98% | 95% | 280 | 100% | 101% | 100% | 98% | 94%
|  | 30 | 87% | 93% | 96% | 98% | 97% | 94% | 88% | 81% | 73% | 63% |  | 290 | 100% | 100% | 100% | 97% | 93% |  | 290 | 100% | 102% | 102% | 100% | 98% |  | 290 | 100% | 104% | 106% | 106% | 105% |  | 290 | 100% | 105% | 109% | 111% | 111% |  | 290 | 100% | 108% | 114% | 118% | 120% | 290 | 100% | 109% | 115% | 120% | 123% | 290 | 100% | 109% | 115% | 121% | 123% | 290 | 100% | 106% | 111% | 114% | 115% | 290 | 100% | 104% | 107% | 108% | 108% | 290 | 100% | 102% | 103% | 103% | 100% | 290 | 100% | 101% | 101% | 99% | 96% | 290 | 100% | 101% | 100% | 98% | 93%
|  | 40 | 87% | 92% | 95% | 96% | 95% | 91% | 86% | 79% | 71% | 63% |  | 300 | 100% | 101% | 100% | 97% | 93% |  | 300 | 100% | 103% | 103% | 102% | 99% |  | 300 | 100% | 105% | 108% | 109% | 108% |  | 300 | 100% | 107% | 113% | 117% | 118% |  | 300 | 100% | 111% | 120% | 126% | 130% | 300 | 100% | 112% | 122% | 130% | 134% | 300 | 100% | 113% | 122% | 129% | 134% | 300 | 100% | 109% | 116% | 120% | 123% | 300 | 100% | 106% | 110% | 112% | 112% | 300 | 100% | 103% | 105% | 104% | 102% | 300 | 100% | 102% | 101% | 99% | 96% | 300 | 100% | 101% | 100% | 97% | 93%
|  | 50 | 87% | 91% | 94% | 94% | 92% | 89% | 84% | 77% | 69% | 61% |  | 310 | 100% | 101% | 100% | 97% | 93% |  | 310 | 100% | 103% | 104% | 103% | 100% |  | 310 | 100% | 106% | 110% | 112% | 110% |  | 310 | 100% | 109% | 117% | 121% | 123% |  | 310 | 100% | 114% | 126% | 134% | 139% | 310 | 100% | 115% | 128% | 138% | 145% | 310 | 100% | 115% | 128% | 137% | 144% | 310 | 100% | 111% | 120% | 127% | 130% | 310 | 100% | 108% | 113% | 116% | 116% | 310 | 100% | 104% | 106% | 106% | 104% | 310 | 100% | 102% | 101% | 99% | 96% | 310 | 100% | 101% | 100% | 97% | 92%
|  | 60 | 87% | 90% | 92% | 91% | 89% | 86% | 80% | 74% | 67% | 60% |  | 320 | 100% | 101% | 100% | 97% | 92% |  | 320 | 100% | 103% | 105% | 104% | 100% |  | 320 | 100% | 107% | 112% | 114% | 113% |  | 320 | 100% | 111% | 119% | 125% | 129% |  | 320 | 100% | 117% | 130% | 141% | 148% | 320 | 100% | 118% | 134% | 146% | 156% | 320 | 100% | 118% | 134% | 145% | 154% | 320 | 100% | 113% | 124% | 132% | 137% | 320 | 100% | 109% | 115% | 118% | 120% | 320 | 100% | 104% | 107% | 107% | 105% | 320 | 100% | 102% | 102% | 100% | 96% | 320 | 100% | 101% | 100% | 96% | 91%
|  | 70 | 87% | 89% | 90% | 89% | 86% | 82% | 77% | 71% | 64% | 57% |  | 330 | 100% | 101% | 100% | 97% | 92% |  | 330 | 100% | 104% | 105% | 104% | 101% |  | 330 | 100% | 108% | 113% | 115% | 115% |  | 330 | 100% | 112% | 122% | 129% | 133% |  | 330 | 100% | 118% | 134% | 146% | 155% | 330 | 100% | 121% | 138% | 154% | 164% | 330 | 100% | 120% | 138% | 152% | 162% | 330 | 100% | 115% | 127% | 136% | 143% | 330 | 100% | 110% | 117% | 121% | 122% | 330 | 100% | 105% | 107% | 108% | 105% | 330 | 100% | 102% | 101% | 99% | 95% | 330 | 100% | 101% | 99% | 96% | 90%
|  | 80 | 87% | 88% | 88% | 86% | 82% | 78% | 73% | 68% | 61% | 55% |  | 340 | 100% | 101% | 100% | 97% | 91% |  | 340 | 100% | 104% | 105% | 104% | 101% |  | 340 | 100% | 108% | 114% | 116% | 116% |  | 340 | 100% | 113% | 124% | 132% | 136% |  | 340 | 100% | 120% | 137% | 151% | 161% | 340 | 100% | 122% | 142% | 159% | 170% | 340 | 100% | 122% | 141% | 156% | 167% | 340 | 100% | 116% | 130% | 141% | 147% | 340 | 100% | 110% | 118% | 123% | 124% | 340 | 100% | 105% | 108% | 108% | 106% | 340 | 100% | 102% | 101% | 99% | 94% | 340 | 100% | 100% | 99% | 95% | 89%
|  | 90 | 87% | 87% | 86% | 82% | 79% | 74% | 69% | 64% | 58% | 52% |  | 350 | 100% | 101% | 100% | 96% | 91% |  | 350 | 100% | 104% | 105% | 104% | 101% |  | 350 | 100% | 108% | 114% | 117% | 117% |  | 350 | 100% | 114% | 125% | 133% | 138% |  | 350 | 100% | 121% | 139% | 154% | 164% | 350 | 100% | 123% | 144% | 162% | 174% | 350 | 100% | 123% | 143% | 159% | 171% | 350 | 100% | 117% | 131% | 143% | 150% | 350 | 100% | 111% | 119% | 124% | 126% | 350 | 100% | 105% | 108% | 108% | 106% | 350 | 100% | 102% | 101% | 99% | 94% | 350 | 100% | 100% | 98% | 94% | 88%
|  | 100 | 87% | 86% | 84% | 80% | 75% | 70% | 65% | 60% | 54% | 48% |  | 0 | 100% | 101% | 100% | 96% | 90% |  | 0 | 100% | 104% | 105% | 104% | 100% |  | 0 | 100% | 108% | 114% | 117% | 117% |  | 0 | 100% | 114% | 125% | 134% | 139% |  | 0 | 100% | 121% | 139% | 155% | 165% | 0 | 100% | 124% | 144% | 163% | 176% | 0 | 100% | 124% | 144% | 160% | 173% | 0 | 100% | 117% | 132% | 143% | 150% | 0 | 100% | 111% | 119% | 124% | 126% | 0 | 100% | 105% | 108% | 108% | 106% | 0 | 100% | 102% | 101% | 99% | 93% | 0 | 100% | 100% | 98% | 94% | 88%
|  | 110 | 87% | 85% | 81% | 77% | 71% | 66% | 61% | 55% | 50% | 44% |  | 10 | 100% | 101% | 100% | 96% | 91% |  | 10 | 100% | 104% | 105% | 104% | 100% |  | 10 | 100% | 108% | 114% | 116% | 116% |  | 10 | 100% | 114% | 125% | 133% | 138% |  | 10 | 100% | 121% | 139% | 154% | 164% | 10 | 100% | 123% | 144% | 162% | 175% | 10 | 100% | 123% | 143% | 159% | 171% | 10 | 100% | 117% | 131% | 143% | 150% | 10 | 100% | 110% | 118% | 123% | 126% | 10 | 100% | 105% | 108% | 108% | 105% | 10 | 100% | 102% | 101% | 98% | 93% | 10 | 100% | 100% | 98% | 94% | 88%
|  | 120 | 87% | 84% | 79% | 73% | 68% | 62% | 56% | 51% | 45% | 40% |  | 20 | 100% | 101% | 100% | 96% | 91% |  | 20 | 100% | 104% | 105% | 104% | 100% |  | 20 | 100% | 108% | 113% | 115% | 115% |  | 20 | 100% | 113% | 124% | 131% | 136% |  | 20 | 100% | 120% | 137% | 150% | 161% | 20 | 100% | 122% | 142% | 159% | 171% | 20 | 100% | 122% | 141% | 156% | 167% | 20 | 100% | 116% | 130% | 140% | 147% | 20 | 100% | 110% | 117% | 122% | 123% | 20 | 100% | 105% | 107% | 107% | 105% | 20 | 100% | 102% | 101% | 98% | 93% | 20 | 100% | 100% | 98% | 94% | 88%
|  | 130 | 87% | 83% | 77% | 71% | 64% | 57% | 52% | 46% | 41% | 37% |  | 30 | 100% | 101% | 100% | 97% | 92% |  | 30 | 100% | 103% | 105% | 103% | 100% |  | 30 | 100% | 107% | 112% | 114% | 114% |  | 30 | 100% | 112% | 122% | 129% | 133% |  | 30 | 100% | 118% | 134% | 146% | 155% | 30 | 100% | 121% | 139% | 154% | 165% | 30 | 100% | 120% | 137% | 152% | 162% | 30 | 100% | 115% | 127% | 136% | 143% | 30 | 100% | 109% | 116% | 120% | 121% | 30 | 100% | 104% | 106% | 107% | 104% | 30 | 100% | 101% | 101% | 98% | 94% | 30 | 100% | 100% | 98% | 94% | 89%
|  | 140 | 87% | 82% | 76% | 68% | 61% | 54% | 47% | 42% | 37% | 34% |  | 40 | 100% | 101% | 100% | 97% | 92% |  | 40 | 100% | 103% | 104% | 102% | 100% |  | 40 | 100% | 107% | 110% | 112% | 112% |  | 40 | 100% | 111% | 119% | 125% | 128% |  | 40 | 100% | 117% | 130% | 140% | 148% | 40 | 100% | 118% | 134% | 147% | 156% | 40 | 100% | 118% | 134% | 145% | 154% | 40 | 100% | 113% | 124% | 132% | 137% | 40 | 100% | 108% | 114% | 117% | 118% | 40 | 100% | 104% | 105% | 106% | 103% | 40 | 100% | 101% | 101% | 98% | 94% | 40 | 100% | 100% | 98% | 94% | 89%
|  | 150 | 87% | 81% | 74% | 66% | 58% | 50% | 44% | 38% | 34% | 30% |  | 50 | 100% | 101% | 100% | 97% | 92% |  | 50 | 100% | 102% | 103% | 102% | 99% |  | 50 | 100% | 105% | 108% | 110% | 109% |  | 50 | 100% | 109% | 116% | 121% | 123% |  | 50 | 100% | 114% | 125% | 134% | 139% | 50 | 100% | 116% | 129% | 139% | 146% | 50 | 100% | 115% | 128% | 137% | 144% | 50 | 100% | 111% | 120% | 127% | 130% | 50 | 100% | 107% | 111% | 114% | 114% | 50 | 100% | 103% | 104% | 104% | 102% | 50 | 100% | 101% | 100% | 98% | 94% | 50 | 100% | 100% | 98% | 95% | 90%
|  | 160 | 87% | 81% | 73% | 65% | 56% | 48% | 41% | 35% | 31% | 28% |  | 60 | 100% | 100% | 100% | 97% | 92% |  | 60 | 100% | 102% | 102% | 100% | 97% |  | 60 | 100% | 104% | 107% | 107% | 105% |  | 60 | 100% | 107% | 113% | 116% | 117% |  | 60 | 100% | 111% | 120% | 126% | 130% | 60 | 100% | 112% | 123% | 131% | 135% | 60 | 100% | 113% | 122% | 129% | 134% | 60 | 100% | 109% | 116% | 120% | 123% | 60 | 100% | 105% | 109% | 110% | 110% | 60 | 100% | 102% | 103% | 102% | 100% | 60 | 100% | 101% | 100% | 98% | 94% | 60 | 100% | 100% | 98% | 95% | 90%
|  | 170 | 87% | 81% | 73% | 64% | 55% | 47% | 39% | 34% | 29% | 27% |  | 70 | 100% | 100% | 99% | 96% | 92% |  | 70 | 100% | 101% | 101% | 100% | 96% |  | 70 | 100% | 103% | 104% | 104% | 103% |  | 70 | 100% | 105% | 109% | 111% | 111% |  | 70 | 100% | 108% | 114% | 118% | 119% | 70 | 100% | 109% | 116% | 121% | 124% | 70 | 100% | 109% | 115% | 121% | 123% | 70 | 100% | 106% | 111% | 114% | 115% | 70 | 100% | 103% | 106% | 107% | 105% | 70 | 100% | 101% | 102% | 100% | 98% | 70 | 100% | 101% | 100% | 97% | 93% | 70 | 100% | 100% | 98% | 95% | 90%
|  | 180 | 87% | 81% | 73% | 63% | 54% | 46% | 39% | 33% | 28% | 26% |  | 80 | 100% | 100% | 99% | 96% | 92% |  | 80 | 100% | 101% | 100% | 98% | 95% |  | 80 | 100% | 102% | 102% | 101% | 98% |  | 80 | 100% | 103% | 105% | 105% | 104% |  | 80 | 100% | 105% | 108% | 109% | 110% | 80 | 100% | 105% | 109% | 111% | 112% | 80 | 100% | 105% | 109% | 111% | 112% | 80 | 100% | 103% | 106% | 107% | 106% | 80 | 100% | 102% | 103% | 102% | 100% | 80 | 100% | 101% | 100% | 99% | 96% | 80 | 100% | 100% | 99% | 96% | 93% | 80 | 100% | 100% | 98% | 95% | 90%
|  | 190 | 87% | 81% | 73% | 64% | 55% | 47% | 40% | 34% | 29% | 27% |  | 90 | 100% | 100% | 98% | 96% | 91% |  | 90 | 100% | 100% | 99% | 96% | 92% |  | 90 | 100% | 101% | 99% | 97% | 94% |  | 90 | 100% | 101% | 100% | 99% | 97% |  | 90 | 100% | 101% | 102% | 101% | 99% | 90 | 100% | 101% | 102% | 102% | 100% | 90 | 100% | 101% | 102% | 101% | 100% | 90 | 100% | 101% | 101% | 99% | 98% | 90 | 100% | 100% | 99% | 97% | 95% | 90 | 100% | 100% | 99% | 96% | 93% | 90 | 100% | 100% | 98% | 95% | 91% | 90 | 100% | 100% | 98% | 94% | 90%
|  | 200 | 87% | 81% | 74% | 65% | 56% | 48% | 41% | 35% | 31% | 28%
|  | 210 | 87% | 82% | 74% | 66% | 59% | 51% | 44% | 38% | 34% | 30%
|  | 220 | 87% | 82% | 76% | 69% | 61% | 54% | 48% | 43% | 38% | 34%
|  | 230 | 87% | 83% | 78% | 71% | 65% | 59% | 52% | 47% | 41% | 37%
|  | 240 | 87% | 84% | 80% | 74% | 69% | 63% | 57% | 52% | 46% | 41%
|  | 250 | 87% | 85% | 82% | 77% | 72% | 67% | 62% | 56% | 51% | 45%
|  | 260 | 87% | 86% | 84% | 80% | 76% | 71% | 66% | 61% | 55% | 49%
|  | 270 | 87% | 87% | 86% | 84% | 80% | 76% | 71% | 65% | 59% | 53%
|  | 280 | 87% | 88% | 88% | 87% | 84% | 79% | 74% | 69% | 62% | 56%
|  | 290 | 87% | 89% | 90% | 89% | 87% | 83% | 78% | 72% | 66% | 59%
|  | 300 | 87% | 90% | 92% | 92% | 90% | 87% | 81% | 76% | 69% | 61%
|  | 310 | 87% | 91% | 94% | 94% | 93% | 89% | 85% | 78% | 71% | 62%
|  | 320 | 87% | 93% | 95% | 96% | 95% | 92% | 87% | 80% | 72% | 63%
|  | 330 | 87% | 93% | 97% | 98% | 97% | 94% | 89% | 82% | 74% | 64%
|  | 340 | 87% | 94% | 97% | 99% | 98% | 96% | 90% | 84% | 75% | 65%
|  | 350 | 87% | 94% | 98% | 100% | 99% | 97% | 91% | 84% | 75% | 65%
|  | 7.6 MELBOURNE | [11 empty] | MELBOURNE
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | MELBOURNE - Janurary | [6 empty] | MELBOURNE - February | [6 empty] | MELBOURNE - March | [6 empty] | MELBOURNE - April | [6 empty] | MELBOURNE - May | [5 empty] | MELBOURNE - June | [5 empty] | MELBOURNE - July | [5 empty] | MELBOURNE - August | [5 empty] | MELBOURNE - September | [5 empty] | MELBOURNE - October | [5 empty] | MELBOURNE - November | [5 empty] | MELBOURNE - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 86% | 93% | 98% | 100% | 100% | 98% | 93% | 86% | 77% | 67% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 86% | 92% | 97% | 99% | 99% | 97% | 92% | 85% | 77% | 67% |  | 270 | 100% | 101% | 100% | 98% | 95% |  | 270 | 100% | 101% | 101% | 99% | 96% |  | 270 | 100% | 102% | 101% | 100% | 98% |  | 270 | 100% | 102% | 102% | 101% | 99% |  | 270 | 100% | 101% | 102% | 102% | 101% | 270 | 100% | 101% | 103% | 101% | 101% | 270 | 100% | 101% | 101% | 102% | 101% | 270 | 100% | 101% | 102% | 101% | 99% | 270 | 100% | 101% | 101% | 101% | 99% | 270 | 100% | 101% | 101% | 100% | 97% | 270 | 100% | 101% | 100% | 98% | 95% | 270 | 100% | 101% | 100% | 97% | 93%
|  | 20 | 86% | 92% | 96% | 99% | 98% | 96% | 91% | 84% | 76% | 67% |  | 280 | 100% | 102% | 101% | 99% | 96% |  | 280 | 100% | 102% | 102% | 101% | 98% |  | 280 | 100% | 103% | 104% | 104% | 103% |  | 280 | 100% | 104% | 106% | 107% | 107% |  | 280 | 100% | 104% | 109% | 111% | 112% | 280 | 100% | 106% | 109% | 113% | 113% | 280 | 100% | 105% | 108% | 111% | 113% | 280 | 100% | 104% | 107% | 108% | 109% | 280 | 100% | 103% | 105% | 105% | 104% | 280 | 100% | 102% | 103% | 102% | 100% | 280 | 100% | 101% | 101% | 100% | 97% | 280 | 100% | 101% | 100% | 98% | 94%
|  | 30 | 86% | 92% | 95% | 97% | 96% | 94% | 89% | 83% | 75% | 66% |  | 290 | 100% | 102% | 102% | 100% | 97% |  | 290 | 100% | 103% | 104% | 103% | 100% |  | 290 | 100% | 104% | 107% | 108% | 107% |  | 290 | 100% | 106% | 111% | 113% | 114% |  | 290 | 100% | 107% | 115% | 119% | 122% | 290 | 100% | 110% | 117% | 122% | 126% | 290 | 100% | 108% | 116% | 121% | 124% | 290 | 100% | 107% | 112% | 115% | 117% | 290 | 100% | 105% | 108% | 110% | 109% | 290 | 100% | 103% | 105% | 105% | 103% | 290 | 100% | 102% | 102% | 101% | 98% | 290 | 100% | 101% | 100% | 98% | 95%
|  | 40 | 86% | 91% | 94% | 95% | 95% | 92% | 87% | 81% | 74% | 65% |  | 300 | 100% | 102% | 102% | 100% | 97% |  | 300 | 100% | 103% | 105% | 105% | 103% |  | 300 | 100% | 106% | 110% | 111% | 111% |  | 300 | 100% | 108% | 115% | 119% | 121% |  | 300 | 100% | 111% | 120% | 128% | 132% | 300 | 100% | 113% | 124% | 132% | 137% | 300 | 100% | 111% | 122% | 130% | 134% | 300 | 100% | 110% | 117% | 122% | 125% | 300 | 100% | 107% | 111% | 113% | 114% | 300 | 100% | 104% | 106% | 107% | 105% | 300 | 100% | 102% | 103% | 101% | 98% | 300 | 100% | 101% | 100% | 98% | 94%
|  | 50 | 86% | 90% | 92% | 93% | 92% | 89% | 85% | 79% | 71% | 63% |  | 310 | 100% | 102% | 102% | 101% | 97% |  | 310 | 100% | 104% | 106% | 106% | 104% |  | 310 | 100% | 107% | 112% | 114% | 115% |  | 310 | 100% | 111% | 118% | 124% | 127% |  | 310 | 100% | 114% | 126% | 135% | 140% | 310 | 100% | 117% | 131% | 141% | 149% | 310 | 100% | 115% | 128% | 138% | 145% | 310 | 100% | 112% | 121% | 128% | 132% | 310 | 100% | 108% | 114% | 117% | 119% | 310 | 100% | 105% | 108% | 109% | 107% | 310 | 100% | 103% | 103% | 102% | 99% | 310 | 100% | 101% | 100% | 98% | 94%
|  | 60 | 86% | 89% | 91% | 91% | 89% | 86% | 81% | 76% | 69% | 61% |  | 320 | 100% | 102% | 102% | 100% | 97% |  | 320 | 100% | 104% | 107% | 107% | 105% |  | 320 | 100% | 108% | 114% | 117% | 117% |  | 320 | 100% | 112% | 122% | 129% | 132% |  | 320 | 100% | 116% | 130% | 141% | 149% | 320 | 100% | 119% | 136% | 150% | 159% | 320 | 100% | 118% | 133% | 145% | 154% | 320 | 100% | 114% | 125% | 133% | 139% | 320 | 100% | 109% | 116% | 120% | 121% | 320 | 100% | 106% | 109% | 110% | 109% | 320 | 100% | 103% | 103% | 102% | 99% | 320 | 100% | 101% | 100% | 98% | 93%
|  | 70 | 86% | 88% | 89% | 88% | 86% | 82% | 78% | 73% | 66% | 59% |  | 330 | 100% | 102% | 102% | 100% | 96% |  | 330 | 100% | 105% | 107% | 107% | 105% |  | 330 | 100% | 109% | 115% | 119% | 120% |  | 330 | 100% | 114% | 124% | 133% | 137% |  | 330 | 100% | 118% | 134% | 147% | 155% | 330 | 100% | 122% | 141% | 156% | 168% | 330 | 100% | 120% | 138% | 152% | 162% | 330 | 100% | 116% | 128% | 138% | 144% | 330 | 100% | 110% | 117% | 123% | 125% | 330 | 100% | 106% | 110% | 111% | 110% | 330 | 100% | 103% | 103% | 102% | 98% | 330 | 100% | 101% | 100% | 97% | 93%
|  | 80 | 86% | 87% | 87% | 85% | 82% | 78% | 74% | 68% | 63% | 56% |  | 340 | 100% | 102% | 102% | 100% | 95% |  | 340 | 100% | 105% | 107% | 108% | 105% |  | 340 | 100% | 109% | 116% | 120% | 121% |  | 340 | 100% | 115% | 127% | 135% | 141% |  | 340 | 100% | 119% | 137% | 151% | 161% | 340 | 100% | 124% | 145% | 162% | 174% | 340 | 100% | 122% | 141% | 156% | 168% | 340 | 100% | 117% | 131% | 141% | 148% | 340 | 100% | 111% | 119% | 124% | 126% | 340 | 100% | 106% | 110% | 111% | 110% | 340 | 100% | 103% | 103% | 102% | 98% | 340 | 100% | 101% | 100% | 97% | 92%
|  | 90 | 86% | 85% | 84% | 82% | 78% | 74% | 70% | 64% | 59% | 53% |  | 350 | 100% | 102% | 102% | 99% | 94% |  | 350 | 100% | 105% | 108% | 108% | 105% |  | 350 | 100% | 110% | 117% | 121% | 122% |  | 350 | 100% | 115% | 127% | 137% | 144% |  | 350 | 100% | 120% | 138% | 153% | 164% | 350 | 100% | 126% | 147% | 165% | 179% | 350 | 100% | 123% | 143% | 160% | 172% | 350 | 100% | 118% | 132% | 144% | 152% | 350 | 100% | 111% | 120% | 125% | 128% | 350 | 100% | 106% | 110% | 112% | 110% | 350 | 100% | 103% | 103% | 101% | 97% | 350 | 100% | 101% | 100% | 97% | 91%
|  | 100 | 86% | 84% | 82% | 78% | 74% | 70% | 65% | 60% | 55% | 49% |  | 0 | 100% | 102% | 101% | 99% | 93% |  | 0 | 100% | 105% | 107% | 107% | 105% |  | 0 | 100% | 110% | 117% | 121% | 122% |  | 0 | 100% | 115% | 128% | 137% | 144% |  | 0 | 100% | 120% | 139% | 154% | 165% | 0 | 100% | 126% | 147% | 167% | 181% | 0 | 100% | 123% | 144% | 161% | 174% | 0 | 100% | 118% | 132% | 145% | 153% | 0 | 100% | 111% | 120% | 125% | 128% | 0 | 100% | 106% | 110% | 111% | 110% | 0 | 100% | 103% | 103% | 101% | 97% | 0 | 100% | 101% | 100% | 96% | 90%
|  | 110 | 86% | 84% | 80% | 75% | 71% | 65% | 61% | 56% | 50% | 45% |  | 10 | 100% | 102% | 101% | 98% | 93% |  | 10 | 100% | 105% | 107% | 107% | 104% |  | 10 | 100% | 110% | 116% | 120% | 121% |  | 10 | 100% | 115% | 127% | 137% | 143% |  | 10 | 100% | 120% | 138% | 153% | 164% | 10 | 100% | 126% | 147% | 165% | 179% | 10 | 100% | 123% | 143% | 160% | 172% | 10 | 100% | 118% | 132% | 144% | 152% | 10 | 100% | 111% | 119% | 125% | 127% | 10 | 100% | 106% | 110% | 111% | 109% | 10 | 100% | 103% | 103% | 101% | 96% | 10 | 100% | 101% | 100% | 96% | 90%
|  | 120 | 86% | 82% | 78% | 72% | 67% | 61% | 56% | 51% | 46% | 42% |  | 20 | 100% | 102% | 101% | 98% | 93% |  | 20 | 100% | 104% | 106% | 106% | 103% |  | 20 | 100% | 109% | 115% | 119% | 120% |  | 20 | 100% | 115% | 126% | 135% | 140% |  | 20 | 100% | 119% | 136% | 150% | 161% | 20 | 100% | 124% | 145% | 163% | 176% | 20 | 100% | 122% | 141% | 156% | 169% | 20 | 100% | 117% | 131% | 141% | 149% | 20 | 100% | 111% | 119% | 123% | 125% | 20 | 100% | 106% | 109% | 110% | 109% | 20 | 100% | 103% | 103% | 100% | 96% | 20 | 100% | 101% | 100% | 96% | 91%
|  | 130 | 86% | 81% | 76% | 69% | 63% | 57% | 51% | 46% | 42% | 37% |  | 30 | 100% | 101% | 100% | 98% | 93% |  | 30 | 100% | 104% | 106% | 105% | 103% |  | 30 | 100% | 108% | 114% | 117% | 118% |  | 30 | 100% | 114% | 124% | 132% | 137% |  | 30 | 100% | 118% | 133% | 146% | 154% | 30 | 100% | 123% | 142% | 158% | 169% | 30 | 100% | 121% | 138% | 152% | 162% | 30 | 100% | 116% | 129% | 139% | 145% | 30 | 100% | 110% | 117% | 121% | 123% | 30 | 100% | 105% | 108% | 109% | 107% | 30 | 100% | 102% | 102% | 100% | 96% | 30 | 100% | 101% | 100% | 97% | 91%
|  | 140 | 86% | 81% | 74% | 67% | 59% | 53% | 47% | 42% | 38% | 34% |  | 40 | 100% | 101% | 100% | 97% | 93% |  | 40 | 100% | 103% | 105% | 104% | 101% |  | 40 | 100% | 107% | 113% | 115% | 115% |  | 40 | 100% | 112% | 121% | 128% | 132% |  | 40 | 100% | 116% | 130% | 140% | 148% | 40 | 100% | 121% | 137% | 151% | 162% | 40 | 100% | 118% | 133% | 146% | 155% | 40 | 100% | 114% | 125% | 133% | 139% | 40 | 100% | 109% | 115% | 119% | 120% | 40 | 100% | 105% | 107% | 108% | 106% | 40 | 100% | 102% | 102% | 100% | 96% | 40 | 100% | 101% | 99% | 97% | 92%
|  | 150 | 86% | 80% | 73% | 65% | 57% | 49% | 43% | 38% | 35% | 31% |  | 50 | 100% | 101% | 100% | 97% | 93% |  | 50 | 100% | 103% | 104% | 103% | 100% |  | 50 | 100% | 106% | 110% | 112% | 112% |  | 50 | 100% | 110% | 118% | 124% | 127% |  | 50 | 100% | 113% | 124% | 133% | 138% | 50 | 100% | 118% | 132% | 144% | 151% | 50 | 100% | 115% | 129% | 139% | 146% | 50 | 100% | 112% | 122% | 129% | 132% | 50 | 100% | 107% | 113% | 115% | 116% | 50 | 100% | 104% | 106% | 106% | 104% | 50 | 100% | 102% | 101% | 99% | 96% | 50 | 100% | 101% | 99% | 97% | 92%
|  | 160 | 86% | 80% | 72% | 63% | 54% | 47% | 40% | 35% | 32% | 29% |  | 60 | 100% | 100% | 99% | 96% | 92% |  | 60 | 100% | 102% | 103% | 101% | 98% |  | 60 | 100% | 105% | 108% | 109% | 108% |  | 60 | 100% | 108% | 115% | 118% | 120% |  | 60 | 100% | 111% | 119% | 126% | 130% | 60 | 100% | 114% | 126% | 135% | 141% | 60 | 100% | 113% | 123% | 130% | 136% | 60 | 100% | 110% | 118% | 123% | 125% | 60 | 100% | 106% | 110% | 112% | 112% | 60 | 100% | 103% | 104% | 104% | 102% | 60 | 100% | 101% | 100% | 98% | 95% | 60 | 100% | 100% | 99% | 96% | 92%
|  | 170 | 86% | 80% | 71% | 63% | 54% | 46% | 39% | 33% | 29% | 27% |  | 70 | 100% | 100% | 98% | 95% | 92% |  | 70 | 100% | 101% | 101% | 99% | 96% |  | 70 | 100% | 103% | 105% | 105% | 104% |  | 70 | 100% | 106% | 110% | 112% | 114% |  | 70 | 100% | 107% | 114% | 118% | 120% | 70 | 100% | 110% | 118% | 126% | 128% | 70 | 100% | 109% | 116% | 122% | 125% | 70 | 100% | 107% | 113% | 116% | 118% | 70 | 100% | 105% | 107% | 108% | 107% | 70 | 100% | 102% | 102% | 102% | 100% | 70 | 100% | 101% | 100% | 98% | 94% | 70 | 100% | 100% | 99% | 96% | 92%
|  | 180 | 86% | 80% | 71% | 62% | 54% | 46% | 39% | 33% | 29% | 27% |  | 80 | 100% | 100% | 98% | 95% | 90% |  | 80 | 100% | 100% | 100% | 97% | 94% |  | 80 | 100% | 102% | 102% | 102% | 99% |  | 80 | 100% | 103% | 105% | 107% | 106% |  | 80 | 100% | 104% | 107% | 110% | 111% | 80 | 100% | 106% | 112% | 115% | 117% | 80 | 100% | 106% | 109% | 113% | 114% | 80 | 100% | 104% | 108% | 110% | 110% | 80 | 100% | 103% | 103% | 103% | 102% | 80 | 100% | 101% | 101% | 99% | 97% | 80 | 100% | 100% | 99% | 96% | 93% | 80 | 100% | 100% | 98% | 96% | 92%
|  | 190 | 86% | 80% | 72% | 63% | 54% | 47% | 40% | 33% | 30% | 28% |  | 90 | 100% | 99% | 97% | 93% | 89% |  | 90 | 100% | 100% | 98% | 95% | 91% |  | 90 | 100% | 101% | 99% | 97% | 95% |  | 90 | 100% | 101% | 101% | 100% | 98% |  | 90 | 100% | 101% | 101% | 101% | 100% | 90 | 100% | 103% | 104% | 104% | 104% | 90 | 100% | 101% | 102% | 102% | 102% | 90 | 100% | 102% | 102% | 102% | 101% | 90 | 100% | 101% | 100% | 99% | 96% | 90 | 100% | 100% | 99% | 96% | 93% | 90 | 100% | 100% | 98% | 95% | 91% | 90 | 100% | 100% | 98% | 95% | 91%
|  | 200 | 86% | 80% | 73% | 64% | 56% | 49% | 42% | 36% | 33% | 30%
|  | 210 | 86% | 81% | 74% | 66% | 58% | 51% | 45% | 40% | 36% | 33%
|  | 220 | 86% | 81% | 75% | 68% | 62% | 55% | 50% | 44% | 40% | 36%
|  | 230 | 86% | 82% | 77% | 71% | 65% | 60% | 54% | 49% | 44% | 40%
|  | 240 | 86% | 83% | 80% | 75% | 70% | 64% | 59% | 54% | 49% | 44%
|  | 250 | 86% | 84% | 82% | 78% | 74% | 69% | 64% | 59% | 54% | 49%
|  | 260 | 86% | 85% | 84% | 81% | 78% | 74% | 69% | 64% | 58% | 53%
|  | 270 | 86% | 87% | 87% | 85% | 82% | 78% | 74% | 68% | 63% | 56%
|  | 280 | 86% | 88% | 88% | 88% | 85% | 82% | 78% | 73% | 67% | 59%
|  | 290 | 86% | 89% | 91% | 91% | 89% | 86% | 82% | 76% | 70% | 62%
|  | 300 | 86% | 90% | 92% | 93% | 92% | 89% | 85% | 80% | 73% | 64%
|  | 310 | 86% | 91% | 94% | 95% | 95% | 92% | 88% | 82% | 74% | 66%
|  | 320 | 86% | 92% | 95% | 97% | 97% | 95% | 90% | 84% | 76% | 67%
|  | 330 | 86% | 92% | 96% | 99% | 98% | 96% | 92% | 85% | 77% | 68%
|  | 340 | 86% | 92% | 97% | 99% | 99% | 97% | 93% | 86% | 78% | 68%
|  | 350 | 86% | 93% | 98% | 100% | 100% | 98% | 93% | 87% | 78% | 67%
|  | 7.7 ADELAIDE | [11 empty] | ADELAIDE
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | ADELAIDE - Janurary | [6 empty] | ADELAIDE - February | [6 empty] | ADELAIDE - March | [6 empty] | ADELAIDE - April | [6 empty] | ADELAIDE - May | [5 empty] | ADELAIDE - June | [5 empty] | ADELAIDE - July | [5 empty] | ADELAIDE - August | [5 empty] | ADELAIDE - September | [5 empty] | ADELAIDE - October | [5 empty] | ADELAIDE - November | [5 empty] | ADELAIDE - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 87% | 94% | 98% | 100% | 99% | 96% | 91% | 83% | 74% | 63% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 87% | 94% | 98% | 100% | 99% | 96% | 90% | 83% | 74% | 63% |  | 270 | 100% | 101% | 100% | 97% | 93% |  | 270 | 100% | 101% | 100% | 97% | 94% |  | 270 | 100% | 101% | 101% | 100% | 97% |  | 270 | 100% | 101% | 101% | 101% | 99% |  | 270 | 100% | 101% | 102% | 102% | 100% | 270 | 100% | 101% | 102% | 102% | 100% | 270 | 100% | 102% | 103% | 103% | 101% | 270 | 100% | 102% | 102% | 102% | 100% | 270 | 100% | 101% | 102% | 101% | 98% | 270 | 100% | 101% | 100% | 99% | 96% | 270 | 100% | 101% | 100% | 98% | 94% | 270 | 100% | 101% | 100% | 98% | 94%
|  | 20 | 87% | 94% | 97% | 99% | 98% | 94% | 89% | 82% | 73% | 63% |  | 280 | 100% | 101% | 100% | 98% | 94% |  | 280 | 100% | 102% | 101% | 99% | 96% |  | 280 | 100% | 103% | 104% | 104% | 102% |  | 280 | 100% | 104% | 106% | 107% | 107% |  | 280 | 100% | 104% | 108% | 110% | 111% | 280 | 100% | 105% | 110% | 112% | 113% | 280 | 100% | 106% | 110% | 112% | 113% | 280 | 100% | 105% | 108% | 109% | 109% | 280 | 100% | 103% | 105% | 105% | 104% | 280 | 100% | 102% | 102% | 101% | 99% | 280 | 100% | 101% | 101% | 99% | 96% | 280 | 100% | 101% | 100% | 98% | 94%
|  | 30 | 87% | 93% | 96% | 97% | 96% | 93% | 87% | 80% | 72% | 62% |  | 290 | 100% | 101% | 100% | 98% | 95% |  | 290 | 100% | 102% | 102% | 101% | 98% |  | 290 | 100% | 104% | 107% | 107% | 106% |  | 290 | 100% | 106% | 110% | 113% | 114% |  | 290 | 100% | 108% | 114% | 119% | 121% | 290 | 100% | 109% | 116% | 121% | 124% | 290 | 100% | 109% | 116% | 121% | 124% | 290 | 100% | 108% | 113% | 116% | 117% | 290 | 100% | 105% | 108% | 109% | 109% | 290 | 100% | 103% | 104% | 104% | 102% | 290 | 100% | 101% | 101% | 100% | 97% | 290 | 100% | 101% | 100% | 98% | 94%
|  | 40 | 87% | 92% | 95% | 95% | 94% | 91% | 85% | 78% | 71% | 61% |  | 300 | 100% | 101% | 101% | 98% | 95% |  | 300 | 100% | 103% | 103% | 102% | 100% |  | 300 | 100% | 105% | 109% | 110% | 110% |  | 300 | 100% | 108% | 114% | 119% | 121% |  | 300 | 100% | 111% | 120% | 127% | 130% | 300 | 100% | 113% | 123% | 131% | 136% | 300 | 100% | 112% | 122% | 130% | 134% | 300 | 100% | 110% | 117% | 123% | 125% | 300 | 100% | 106% | 111% | 113% | 114% | 300 | 100% | 104% | 105% | 106% | 104% | 300 | 100% | 102% | 102% | 100% | 97% | 300 | 100% | 101% | 100% | 98% | 93%
|  | 50 | 87% | 91% | 93% | 93% | 91% | 88% | 83% | 76% | 69% | 60% |  | 310 | 100% | 101% | 101% | 98% | 94% |  | 310 | 100% | 103% | 104% | 103% | 101% |  | 310 | 100% | 107% | 111% | 113% | 113% |  | 310 | 100% | 110% | 118% | 124% | 127% |  | 310 | 100% | 113% | 125% | 133% | 139% | 310 | 100% | 116% | 129% | 139% | 147% | 310 | 100% | 115% | 128% | 137% | 144% | 310 | 100% | 112% | 121% | 128% | 132% | 310 | 100% | 108% | 113% | 117% | 117% | 310 | 100% | 104% | 107% | 107% | 105% | 310 | 100% | 102% | 102% | 100% | 97% | 310 | 100% | 101% | 100% | 97% | 93%
|  | 60 | 87% | 91% | 92% | 91% | 89% | 85% | 79% | 74% | 66% | 58% |  | 320 | 100% | 101% | 101% | 98% | 93% |  | 320 | 100% | 104% | 105% | 105% | 102% |  | 320 | 100% | 108% | 113% | 116% | 116% |  | 320 | 100% | 112% | 122% | 128% | 131% |  | 320 | 100% | 116% | 129% | 140% | 146% | 320 | 100% | 118% | 134% | 147% | 156% | 320 | 100% | 118% | 133% | 144% | 152% | 320 | 100% | 114% | 125% | 133% | 138% | 320 | 100% | 109% | 116% | 120% | 121% | 320 | 100% | 105% | 108% | 108% | 107% | 320 | 100% | 102% | 102% | 100% | 97% | 320 | 100% | 101% | 100% | 96% | 92%
|  | 70 | 87% | 89% | 90% | 88% | 85% | 81% | 76% | 70% | 63% | 56% |  | 330 | 100% | 101% | 101% | 98% | 93% |  | 330 | 100% | 104% | 106% | 105% | 102% |  | 330 | 100% | 109% | 114% | 118% | 118% |  | 330 | 100% | 113% | 124% | 131% | 136% |  | 330 | 100% | 118% | 133% | 145% | 154% | 330 | 100% | 121% | 139% | 154% | 165% | 330 | 100% | 120% | 137% | 150% | 160% | 330 | 100% | 115% | 128% | 138% | 144% | 330 | 100% | 110% | 117% | 121% | 123% | 330 | 100% | 106% | 109% | 109% | 107% | 330 | 100% | 102% | 102% | 100% | 96% | 330 | 100% | 101% | 99% | 96% | 90%
|  | 80 | 87% | 88% | 87% | 85% | 82% | 77% | 73% | 67% | 60% | 53% |  | 340 | 100% | 101% | 100% | 97% | 92% |  | 340 | 100% | 104% | 106% | 105% | 102% |  | 340 | 100% | 109% | 115% | 119% | 120% |  | 340 | 100% | 114% | 125% | 134% | 139% |  | 340 | 100% | 120% | 136% | 149% | 159% | 340 | 100% | 122% | 143% | 159% | 171% | 340 | 100% | 122% | 140% | 155% | 165% | 340 | 100% | 117% | 130% | 141% | 147% | 340 | 100% | 110% | 118% | 123% | 125% | 340 | 100% | 106% | 109% | 110% | 108% | 340 | 100% | 102% | 102% | 100% | 95% | 340 | 100% | 101% | 99% | 95% | 89%
|  | 90 | 87% | 87% | 85% | 82% | 78% | 74% | 69% | 63% | 57% | 50% |  | 350 | 100% | 101% | 100% | 97% | 91% |  | 350 | 100% | 104% | 106% | 105% | 102% |  | 350 | 100% | 109% | 116% | 120% | 120% |  | 350 | 100% | 114% | 127% | 136% | 141% |  | 350 | 100% | 120% | 138% | 152% | 162% | 350 | 100% | 123% | 145% | 162% | 174% | 350 | 100% | 122% | 142% | 157% | 169% | 350 | 100% | 117% | 132% | 142% | 150% | 350 | 100% | 110% | 118% | 124% | 126% | 350 | 100% | 106% | 109% | 110% | 108% | 350 | 100% | 102% | 102% | 99% | 94% | 350 | 100% | 100% | 99% | 94% | 88%
|  | 100 | 87% | 86% | 83% | 79% | 75% | 70% | 64% | 59% | 53% | 47% |  | 0 | 100% | 101% | 100% | 96% | 90% |  | 0 | 100% | 105% | 106% | 105% | 102% |  | 0 | 100% | 109% | 116% | 120% | 120% |  | 0 | 100% | 115% | 127% | 136% | 142% |  | 0 | 100% | 121% | 138% | 152% | 163% | 0 | 100% | 123% | 145% | 163% | 176% | 0 | 100% | 123% | 142% | 158% | 170% | 0 | 100% | 117% | 132% | 143% | 150% | 0 | 100% | 111% | 119% | 124% | 126% | 0 | 100% | 106% | 109% | 110% | 107% | 0 | 100% | 102% | 101% | 99% | 94% | 0 | 100% | 100% | 98% | 94% | 88%
|  | 110 | 87% | 85% | 81% | 76% | 71% | 65% | 60% | 54% | 49% | 44% |  | 10 | 100% | 101% | 100% | 96% | 90% |  | 10 | 100% | 104% | 106% | 105% | 102% |  | 10 | 100% | 109% | 116% | 119% | 120% |  | 10 | 100% | 114% | 126% | 135% | 141% |  | 10 | 100% | 120% | 138% | 151% | 161% | 10 | 100% | 123% | 145% | 162% | 174% | 10 | 100% | 122% | 141% | 157% | 168% | 10 | 100% | 117% | 131% | 141% | 149% | 10 | 100% | 110% | 118% | 123% | 125% | 10 | 100% | 106% | 109% | 110% | 107% | 10 | 100% | 102% | 101% | 99% | 94% | 10 | 100% | 100% | 98% | 94% | 88%
|  | 120 | 87% | 84% | 79% | 74% | 67% | 61% | 55% | 50% | 45% | 40% |  | 20 | 100% | 101% | 100% | 96% | 90% |  | 20 | 100% | 104% | 106% | 105% | 102% |  | 20 | 100% | 109% | 115% | 118% | 119% |  | 20 | 100% | 114% | 125% | 133% | 138% |  | 20 | 100% | 119% | 136% | 148% | 158% | 20 | 100% | 122% | 143% | 159% | 170% | 20 | 100% | 121% | 139% | 154% | 165% | 20 | 100% | 116% | 129% | 139% | 146% | 20 | 100% | 110% | 117% | 121% | 123% | 20 | 100% | 105% | 108% | 109% | 107% | 20 | 100% | 101% | 101% | 99% | 93% | 20 | 100% | 100% | 98% | 94% | 88%
|  | 130 | 87% | 83% | 77% | 71% | 64% | 57% | 51% | 46% | 41% | 36% |  | 30 | 100% | 101% | 100% | 96% | 91% |  | 30 | 100% | 104% | 105% | 105% | 102% |  | 30 | 100% | 108% | 114% | 117% | 116% |  | 30 | 100% | 112% | 123% | 130% | 133% |  | 30 | 100% | 118% | 132% | 144% | 152% | 30 | 100% | 120% | 138% | 153% | 164% | 30 | 100% | 120% | 136% | 149% | 159% | 30 | 100% | 115% | 126% | 135% | 141% | 30 | 100% | 109% | 116% | 119% | 120% | 30 | 100% | 105% | 108% | 108% | 106% | 30 | 100% | 101% | 101% | 98% | 93% | 30 | 100% | 100% | 98% | 94% | 88%
|  | 140 | 87% | 82% | 76% | 68% | 60% | 53% | 47% | 41% | 37% | 33% |  | 40 | 100% | 101% | 99% | 96% | 91% |  | 40 | 100% | 103% | 105% | 104% | 101% |  | 40 | 100% | 107% | 112% | 114% | 114% |  | 40 | 100% | 111% | 120% | 126% | 129% |  | 40 | 100% | 115% | 129% | 138% | 146% | 40 | 100% | 118% | 134% | 147% | 156% | 40 | 100% | 118% | 132% | 143% | 151% | 40 | 100% | 113% | 123% | 131% | 135% | 40 | 100% | 108% | 113% | 117% | 117% | 40 | 100% | 104% | 107% | 107% | 104% | 40 | 100% | 101% | 100% | 98% | 94% | 40 | 100% | 100% | 98% | 94% | 89%
|  | 150 | 87% | 82% | 75% | 67% | 58% | 50% | 43% | 37% | 33% | 30% |  | 50 | 100% | 101% | 99% | 96% | 91% |  | 50 | 100% | 103% | 104% | 103% | 100% |  | 50 | 100% | 106% | 110% | 111% | 111% |  | 50 | 100% | 109% | 116% | 122% | 124% |  | 50 | 100% | 113% | 124% | 132% | 137% | 50 | 100% | 116% | 129% | 139% | 146% | 50 | 100% | 115% | 127% | 136% | 142% | 50 | 100% | 111% | 120% | 126% | 129% | 50 | 100% | 106% | 111% | 113% | 113% | 50 | 100% | 104% | 105% | 105% | 103% | 50 | 100% | 101% | 100% | 97% | 93% | 50 | 100% | 100% | 98% | 95% | 90%
|  | 160 | 87% | 81% | 74% | 65% | 56% | 48% | 40% | 34% | 30% | 27% |  | 60 | 100% | 100% | 99% | 96% | 92% |  | 60 | 100% | 102% | 103% | 102% | 99% |  | 60 | 100% | 105% | 108% | 109% | 107% |  | 60 | 100% | 107% | 112% | 116% | 117% |  | 60 | 100% | 110% | 119% | 124% | 128% | 60 | 100% | 113% | 122% | 130% | 135% | 60 | 100% | 112% | 121% | 128% | 132% | 60 | 100% | 108% | 115% | 120% | 121% | 60 | 100% | 105% | 108% | 110% | 109% | 60 | 100% | 103% | 104% | 103% | 101% | 60 | 100% | 100% | 100% | 97% | 93% | 60 | 100% | 100% | 98% | 95% | 90%
|  | 170 | 87% | 81% | 74% | 64% | 55% | 47% | 39% | 32% | 28% | 26% |  | 70 | 100% | 100% | 99% | 96% | 91% |  | 70 | 100% | 102% | 102% | 100% | 97% |  | 70 | 100% | 103% | 105% | 105% | 103% |  | 70 | 100% | 105% | 108% | 110% | 110% |  | 70 | 100% | 107% | 113% | 117% | 119% | 70 | 100% | 109% | 116% | 121% | 123% | 70 | 100% | 109% | 115% | 119% | 122% | 70 | 100% | 106% | 111% | 112% | 114% | 70 | 100% | 103% | 105% | 105% | 105% | 70 | 100% | 102% | 102% | 101% | 98% | 70 | 100% | 100% | 99% | 96% | 92% | 70 | 100% | 100% | 98% | 95% | 90%
|  | 180 | 87% | 81% | 74% | 64% | 55% | 47% | 39% | 32% | 27% | 25% |  | 80 | 100% | 100% | 98% | 95% | 91% |  | 80 | 100% | 101% | 100% | 98% | 95% |  | 80 | 100% | 102% | 102% | 101% | 100% |  | 80 | 100% | 103% | 104% | 105% | 103% |  | 80 | 100% | 104% | 106% | 109% | 108% | 80 | 100% | 105% | 109% | 112% | 112% | 80 | 100% | 105% | 108% | 111% | 111% | 80 | 100% | 103% | 105% | 106% | 105% | 80 | 100% | 102% | 102% | 101% | 99% | 80 | 100% | 101% | 100% | 99% | 96% | 80 | 100% | 100% | 98% | 95% | 91% | 80 | 100% | 100% | 98% | 95% | 90%
|  | 190 | 87% | 81% | 74% | 65% | 55% | 47% | 39% | 33% | 28% | 26% |  | 90 | 100% | 100% | 98% | 94% | 90% |  | 90 | 100% | 100% | 99% | 96% | 93% |  | 90 | 100% | 100% | 100% | 97% | 95% |  | 90 | 100% | 100% | 99% | 98% | 96% |  | 90 | 100% | 101% | 101% | 100% | 98% | 90 | 100% | 101% | 101% | 101% | 100% | 90 | 100% | 102% | 102% | 101% | 100% | 90 | 100% | 100% | 100% | 98% | 96% | 90 | 100% | 100% | 99% | 97% | 94% | 90 | 100% | 100% | 99% | 96% | 93% | 90 | 100% | 99% | 97% | 94% | 90% | 90 | 100% | 100% | 98% | 94% | 90%
|  | 200 | 87% | 82% | 75% | 66% | 57% | 49% | 41% | 35% | 31% | 28%
|  | 210 | 87% | 82% | 75% | 68% | 59% | 51% | 44% | 39% | 34% | 31%
|  | 220 | 87% | 83% | 77% | 70% | 62% | 55% | 49% | 43% | 38% | 34%
|  | 230 | 87% | 84% | 78% | 73% | 66% | 59% | 53% | 48% | 42% | 38%
|  | 240 | 87% | 85% | 80% | 75% | 70% | 64% | 58% | 52% | 47% | 42%
|  | 250 | 87% | 86% | 83% | 78% | 74% | 68% | 63% | 57% | 51% | 46%
|  | 260 | 87% | 87% | 85% | 81% | 77% | 73% | 67% | 61% | 55% | 49%
|  | 270 | 87% | 88% | 87% | 84% | 81% | 76% | 72% | 66% | 59% | 53%
|  | 280 | 87% | 89% | 89% | 87% | 85% | 80% | 75% | 70% | 63% | 56%
|  | 290 | 87% | 90% | 91% | 90% | 88% | 84% | 79% | 73% | 66% | 59%
|  | 300 | 87% | 91% | 93% | 93% | 91% | 87% | 82% | 76% | 69% | 61%
|  | 310 | 87% | 92% | 95% | 95% | 94% | 90% | 85% | 79% | 71% | 62%
|  | 320 | 87% | 93% | 96% | 97% | 96% | 93% | 88% | 81% | 73% | 64%
|  | 330 | 87% | 93% | 97% | 98% | 98% | 94% | 89% | 82% | 74% | 64%
|  | 340 | 87% | 94% | 98% | 100% | 99% | 96% | 90% | 83% | 74% | 64%
|  | 350 | 87% | 94% | 98% | 100% | 99% | 96% | 91% | 83% | 74% | 64%
|  | 7.8 ALICE SPRINGS | [11 empty] | Alice Springs
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | Alice Springs - Janurary | [6 empty] | Alice Springs - February | [6 empty] | Alice Springs - March | [6 empty] | Alice Springs - April | [6 empty] | Alice Springs - May | [5 empty] | Alice Springs - June | [5 empty] | Alice Springs - July | [5 empty] | Alice Springs - August | [5 empty] | Alice Springs - September | [5 empty] | Alice Springs - October | [5 empty] | Alice Springs - November | [5 empty] | Alice Springs - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 90% | 96% | 99% | 100% | 98% | 94% | 87% | 78% | 68% | 57% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 90% | 96% | 99% | 100% | 98% | 94% | 87% | 79% | 69% | 57% |  | 270 | 100% | 99% | 97% | 93% | 88% |  | 270 | 100% | 100% | 98% | 94% | 90% |  | 270 | 100% | 100% | 99% | 96% | 92% |  | 270 | 100% | 100% | 99% | 97% | 93% |  | 270 | 100% | 101% | 100% | 98% | 95% | 270 | 100% | 101% | 101% | 99% | 96% | 270 | 100% | 101% | 101% | 99% | 96% | 270 | 100% | 101% | 100% | 98% | 95% | 270 | 100% | 100% | 99% | 97% | 93% | 270 | 100% | 100% | 98% | 95% | 91% | 270 | 100% | 100% | 98% | 94% | 89% | 270 | 100% | 100% | 97% | 94% | 89%
|  | 20 | 90% | 96% | 99% | 100% | 98% | 93% | 87% | 79% | 69% | 58% |  | 280 | 100% | 99% | 97% | 93% | 88% |  | 280 | 100% | 100% | 98% | 95% | 91% |  | 280 | 100% | 101% | 101% | 99% | 96% |  | 280 | 100% | 102% | 103% | 102% | 100% |  | 280 | 100% | 103% | 105% | 105% | 104% | 280 | 100% | 104% | 107% | 107% | 106% | 280 | 100% | 104% | 106% | 107% | 105% | 280 | 100% | 103% | 105% | 104% | 102% | 280 | 100% | 102% | 102% | 100% | 97% | 280 | 100% | 100% | 100% | 97% | 92% | 280 | 100% | 100% | 98% | 94% | 89% | 280 | 100% | 100% | 97% | 93% | 88%
|  | 30 | 90% | 96% | 98% | 99% | 97% | 93% | 87% | 78% | 69% | 59% |  | 290 | 100% | 99% | 96% | 92% | 86% |  | 290 | 100% | 100% | 99% | 96% | 91% |  | 290 | 100% | 103% | 103% | 101% | 98% |  | 290 | 100% | 104% | 106% | 107% | 105% |  | 290 | 100% | 106% | 110% | 112% | 112% | 290 | 100% | 108% | 113% | 115% | 116% | 290 | 100% | 107% | 111% | 114% | 114% | 290 | 100% | 105% | 109% | 110% | 109% | 290 | 100% | 103% | 104% | 104% | 101% | 290 | 100% | 101% | 100% | 98% | 94% | 290 | 100% | 100% | 97% | 93% | 88% | 290 | 100% | 99% | 96% | 92% | 87%
|  | 40 | 90% | 95% | 98% | 98% | 96% | 91% | 86% | 78% | 69% | 60% |  | 300 | 100% | 99% | 96% | 91% | 85% |  | 300 | 100% | 100% | 99% | 96% | 91% |  | 300 | 100% | 103% | 104% | 103% | 100% |  | 300 | 100% | 106% | 110% | 111% | 110% |  | 300 | 100% | 109% | 115% | 119% | 120% | 300 | 100% | 110% | 118% | 124% | 126% | 300 | 100% | 110% | 117% | 122% | 123% | 300 | 100% | 108% | 112% | 115% | 115% | 300 | 100% | 104% | 106% | 106% | 105% | 300 | 100% | 102% | 101% | 99% | 95% | 300 | 100% | 99% | 97% | 93% | 88% | 300 | 100% | 99% | 96% | 91% | 85%
|  | 50 | 90% | 94% | 96% | 96% | 94% | 90% | 84% | 77% | 69% | 60% |  | 310 | 100% | 99% | 95% | 90% | 84% |  | 310 | 100% | 101% | 100% | 96% | 91% |  | 310 | 100% | 104% | 106% | 105% | 103% |  | 310 | 100% | 108% | 112% | 115% | 115% |  | 310 | 100% | 111% | 120% | 125% | 128% | 310 | 100% | 113% | 123% | 131% | 135% | 310 | 100% | 112% | 121% | 128% | 131% | 310 | 100% | 109% | 116% | 119% | 121% | 310 | 100% | 106% | 108% | 109% | 108% | 310 | 100% | 102% | 102% | 100% | 96% | 310 | 100% | 99% | 97% | 93% | 87% | 310 | 100% | 99% | 95% | 90% | 84%
|  | 60 | 90% | 93% | 95% | 94% | 92% | 88% | 82% | 76% | 68% | 60% |  | 320 | 100% | 99% | 95% | 90% | 83% |  | 320 | 100% | 101% | 100% | 96% | 91% |  | 320 | 100% | 105% | 107% | 106% | 104% |  | 320 | 100% | 109% | 115% | 118% | 119% |  | 320 | 100% | 113% | 123% | 130% | 134% | 320 | 100% | 115% | 128% | 137% | 142% | 320 | 100% | 114% | 125% | 134% | 139% | 320 | 100% | 111% | 119% | 123% | 125% | 320 | 100% | 106% | 110% | 111% | 110% | 320 | 100% | 102% | 102% | 100% | 96% | 320 | 100% | 99% | 96% | 92% | 86% | 320 | 100% | 98% | 94% | 89% | 82%
|  | 70 | 90% | 93% | 93% | 92% | 89% | 85% | 80% | 73% | 66% | 59% |  | 330 | 100% | 98% | 95% | 89% | 82% |  | 330 | 100% | 101% | 100% | 97% | 91% |  | 330 | 100% | 105% | 108% | 108% | 105% |  | 330 | 100% | 110% | 117% | 122% | 122% |  | 330 | 100% | 115% | 126% | 134% | 140% | 330 | 100% | 117% | 131% | 142% | 149% | 330 | 100% | 116% | 129% | 139% | 145% | 330 | 100% | 112% | 121% | 127% | 130% | 330 | 100% | 107% | 111% | 113% | 112% | 330 | 100% | 103% | 103% | 101% | 96% | 330 | 100% | 99% | 96% | 91% | 85% | 330 | 100% | 98% | 94% | 88% | 80%
|  | 80 | 90% | 92% | 91% | 90% | 87% | 82% | 77% | 71% | 64% | 57% |  | 340 | 100% | 98% | 94% | 89% | 81% |  | 340 | 100% | 101% | 100% | 97% | 91% |  | 340 | 100% | 106% | 108% | 109% | 106% |  | 340 | 100% | 111% | 119% | 123% | 125% |  | 340 | 100% | 116% | 129% | 138% | 144% | 340 | 100% | 119% | 134% | 146% | 154% | 340 | 100% | 117% | 131% | 142% | 149% | 340 | 100% | 113% | 123% | 130% | 133% | 340 | 100% | 108% | 112% | 114% | 114% | 340 | 100% | 103% | 103% | 101% | 97% | 340 | 100% | 99% | 96% | 91% | 84% | 340 | 100% | 98% | 94% | 87% | 79%
|  | 90 | 90% | 91% | 90% | 87% | 84% | 79% | 73% | 67% | 61% | 54% |  | 350 | 100% | 99% | 94% | 88% | 80% |  | 350 | 100% | 101% | 100% | 97% | 91% |  | 350 | 100% | 106% | 109% | 109% | 107% |  | 350 | 100% | 111% | 120% | 125% | 127% |  | 350 | 100% | 117% | 130% | 140% | 147% | 350 | 100% | 119% | 136% | 149% | 157% | 350 | 100% | 118% | 133% | 145% | 152% | 350 | 100% | 114% | 124% | 131% | 135% | 350 | 100% | 108% | 113% | 115% | 114% | 350 | 100% | 103% | 103% | 101% | 96% | 350 | 100% | 99% | 96% | 91% | 84% | 350 | 100% | 98% | 94% | 87% | 78%
|  | 100 | 90% | 90% | 88% | 84% | 80% | 75% | 69% | 63% | 57% | 51% |  | 0 | 100% | 99% | 95% | 89% | 81% |  | 0 | 100% | 101% | 100% | 97% | 91% |  | 0 | 100% | 106% | 109% | 110% | 107% |  | 0 | 100% | 111% | 120% | 126% | 128% |  | 0 | 100% | 117% | 130% | 141% | 147% | 0 | 100% | 120% | 137% | 149% | 158% | 0 | 100% | 118% | 133% | 145% | 153% | 0 | 100% | 114% | 124% | 132% | 136% | 0 | 100% | 108% | 113% | 115% | 115% | 0 | 100% | 103% | 103% | 101% | 96% | 0 | 100% | 99% | 96% | 91% | 83% | 0 | 100% | 98% | 94% | 87% | 78%
|  | 110 | 90% | 89% | 86% | 82% | 76% | 71% | 65% | 59% | 53% | 47% |  | 10 | 100% | 99% | 95% | 89% | 81% |  | 10 | 100% | 101% | 101% | 97% | 91% |  | 10 | 100% | 106% | 109% | 110% | 107% |  | 10 | 100% | 111% | 120% | 125% | 127% |  | 10 | 100% | 117% | 130% | 140% | 147% | 10 | 100% | 119% | 136% | 148% | 157% | 10 | 100% | 117% | 133% | 144% | 152% | 10 | 100% | 114% | 124% | 131% | 135% | 10 | 100% | 108% | 113% | 115% | 114% | 10 | 100% | 103% | 103% | 101% | 97% | 10 | 100% | 99% | 96% | 91% | 84% | 10 | 100% | 98% | 94% | 87% | 79%
|  | 120 | 90% | 88% | 84% | 79% | 73% | 67% | 60% | 54% | 48% | 42% |  | 20 | 100% | 99% | 95% | 90% | 83% |  | 20 | 100% | 101% | 101% | 97% | 92% |  | 20 | 100% | 106% | 109% | 109% | 107% |  | 20 | 100% | 111% | 119% | 124% | 125% |  | 20 | 100% | 116% | 129% | 138% | 144% | 20 | 100% | 119% | 134% | 146% | 153% | 20 | 100% | 117% | 131% | 142% | 148% | 20 | 100% | 113% | 123% | 129% | 132% | 20 | 100% | 107% | 112% | 114% | 113% | 20 | 100% | 103% | 103% | 101% | 97% | 20 | 100% | 100% | 97% | 92% | 85% | 20 | 100% | 98% | 94% | 88% | 80%
|  | 130 | 90% | 87% | 82% | 76% | 69% | 62% | 55% | 49% | 43% | 38% |  | 30 | 100% | 99% | 96% | 91% | 84% |  | 30 | 100% | 101% | 101% | 98% | 93% |  | 30 | 100% | 106% | 108% | 108% | 106% |  | 30 | 100% | 110% | 117% | 122% | 123% |  | 30 | 100% | 114% | 126% | 134% | 139% | 30 | 100% | 117% | 131% | 142% | 148% | 30 | 100% | 116% | 128% | 137% | 143% | 30 | 100% | 112% | 121% | 126% | 129% | 30 | 100% | 107% | 111% | 113% | 111% | 30 | 100% | 103% | 103% | 101% | 97% | 30 | 100% | 100% | 97% | 93% | 86% | 30 | 100% | 99% | 95% | 90% | 82%
|  | 140 | 90% | 86% | 80% | 73% | 65% | 58% | 50% | 44% | 38% | 33% |  | 40 | 100% | 100% | 97% | 92% | 86% |  | 40 | 100% | 101% | 101% | 98% | 93% |  | 40 | 100% | 105% | 107% | 107% | 105% |  | 40 | 100% | 109% | 115% | 119% | 119% |  | 40 | 100% | 113% | 123% | 130% | 133% | 40 | 100% | 115% | 127% | 136% | 141% | 40 | 100% | 114% | 125% | 133% | 137% | 40 | 100% | 111% | 118% | 123% | 124% | 40 | 100% | 106% | 110% | 111% | 109% | 40 | 100% | 102% | 103% | 100% | 97% | 40 | 100% | 100% | 98% | 94% | 88% | 40 | 100% | 99% | 96% | 91% | 84%
|  | 150 | 90% | 86% | 79% | 71% | 62% | 53% | 46% | 39% | 34% | 29% |  | 50 | 100% | 100% | 98% | 94% | 88% |  | 50 | 100% | 101% | 101% | 98% | 94% |  | 50 | 100% | 104% | 106% | 106% | 103% |  | 50 | 100% | 108% | 113% | 115% | 115% |  | 50 | 100% | 111% | 119% | 124% | 127% | 50 | 100% | 113% | 122% | 129% | 133% | 50 | 100% | 111% | 120% | 127% | 130% | 50 | 100% | 109% | 115% | 118% | 119% | 50 | 100% | 105% | 108% | 108% | 106% | 50 | 100% | 102% | 102% | 100% | 96% | 50 | 100% | 100% | 98% | 94% | 89% | 50 | 100% | 99% | 96% | 92% | 86%
|  | 160 | 90% | 85% | 78% | 69% | 60% | 50% | 42% | 36% | 30% | 26% |  | 60 | 100% | 100% | 98% | 95% | 90% |  | 60 | 100% | 101% | 101% | 98% | 94% |  | 60 | 100% | 103% | 105% | 104% | 102% |  | 60 | 100% | 106% | 110% | 111% | 111% |  | 60 | 100% | 109% | 114% | 118% | 120% | 60 | 100% | 110% | 117% | 122% | 124% | 60 | 100% | 109% | 116% | 120% | 121% | 60 | 100% | 107% | 111% | 114% | 113% | 60 | 100% | 104% | 106% | 106% | 103% | 60 | 100% | 102% | 102% | 99% | 95% | 60 | 100% | 100% | 99% | 95% | 90% | 60 | 100% | 100% | 97% | 93% | 88%
|  | 170 | 90% | 85% | 77% | 68% | 58% | 48% | 40% | 33% | 28% | 24% |  | 70 | 100% | 100% | 99% | 96% | 92% |  | 70 | 100% | 101% | 100% | 98% | 94% |  | 70 | 100% | 103% | 103% | 102% | 99% |  | 70 | 100% | 104% | 106% | 107% | 105% |  | 70 | 100% | 106% | 110% | 112% | 111% | 70 | 100% | 107% | 112% | 115% | 115% | 70 | 100% | 106% | 110% | 113% | 112% | 70 | 100% | 105% | 107% | 108% | 107% | 70 | 100% | 103% | 103% | 103% | 100% | 70 | 100% | 101% | 101% | 98% | 94% | 70 | 100% | 100% | 99% | 96% | 91% | 70 | 100% | 100% | 98% | 95% | 90%
|  | 180 | 90% | 84% | 77% | 67% | 57% | 47% | 40% | 33% | 27% | 22% |  | 80 | 100% | 101% | 100% | 97% | 93% |  | 80 | 100% | 101% | 100% | 97% | 94% |  | 80 | 100% | 102% | 101% | 100% | 96% |  | 80 | 100% | 102% | 103% | 102% | 100% |  | 80 | 100% | 103% | 105% | 105% | 103% | 80 | 100% | 104% | 106% | 106% | 105% | 80 | 100% | 103% | 105% | 105% | 103% | 80 | 100% | 103% | 103% | 103% | 101% | 80 | 100% | 101% | 101% | 99% | 96% | 80 | 100% | 101% | 100% | 97% | 93% | 80 | 100% | 100% | 99% | 96% | 92% | 80 | 100% | 100% | 99% | 96% | 91%
|  | 190 | 90% | 84% | 77% | 68% | 57% | 48% | 40% | 33% | 27% | 23% |  | 90 | 100% | 101% | 100% | 97% | 93% |  | 90 | 100% | 101% | 100% | 97% | 93% |  | 90 | 100% | 100% | 100% | 97% | 93% |  | 90 | 100% | 100% | 100% | 97% | 94% |  | 90 | 100% | 101% | 100% | 97% | 94% | 90 | 100% | 101% | 100% | 97% | 95% | 90 | 100% | 100% | 99% | 96% | 94% | 90 | 100% | 101% | 99% | 96% | 93% | 90 | 100% | 100% | 98% | 96% | 92% | 90 | 100% | 100% | 98% | 96% | 92% | 90 | 100% | 100% | 99% | 96% | 92% | 90 | 100% | 101% | 100% | 97% | 92%
|  | 200 | 90% | 85% | 78% | 69% | 59% | 49% | 41% | 34% | 29% | 25%
|  | 210 | 90% | 85% | 78% | 70% | 61% | 52% | 44% | 38% | 33% | 29%
|  | 220 | 90% | 86% | 80% | 72% | 64% | 56% | 49% | 42% | 37% | 32%
|  | 230 | 90% | 87% | 81% | 74% | 67% | 60% | 53% | 47% | 42% | 37%
|  | 240 | 90% | 87% | 83% | 77% | 71% | 64% | 58% | 52% | 46% | 41%
|  | 250 | 90% | 88% | 84% | 80% | 75% | 69% | 63% | 57% | 51% | 45%
|  | 260 | 90% | 89% | 87% | 83% | 78% | 73% | 67% | 61% | 55% | 49%
|  | 270 | 90% | 90% | 89% | 85% | 81% | 77% | 71% | 65% | 59% | 52%
|  | 280 | 90% | 91% | 90% | 88% | 84% | 80% | 75% | 69% | 62% | 55%
|  | 290 | 90% | 92% | 92% | 91% | 87% | 83% | 78% | 71% | 64% | 57%
|  | 300 | 90% | 93% | 94% | 93% | 90% | 86% | 80% | 73% | 66% | 58%
|  | 310 | 90% | 94% | 95% | 95% | 92% | 88% | 82% | 75% | 67% | 58%
|  | 320 | 90% | 95% | 97% | 96% | 94% | 90% | 84% | 76% | 68% | 58%
|  | 330 | 90% | 95% | 98% | 98% | 96% | 91% | 85% | 77% | 68% | 58%
|  | 340 | 90% | 96% | 98% | 99% | 97% | 93% | 86% | 78% | 68% | 58%
|  | 350 | 90% | 96% | 99% | 100% | 98% | 93% | 87% | 78% | 68% | 57%
|  | 7.9 PERTH | [11 empty] | PERTH
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | PERTH - Janurary | [6 empty] | PERTH - February | [6 empty] | PERTH - March | [6 empty] | PERTH - April | [6 empty] | PERTH - May | [5 empty] | PERTH - June | [5 empty] | PERTH - July | [5 empty] | PERTH - August | [5 empty] | PERTH - September | [5 empty] | PERTH - October | [5 empty] | PERTH - November | [5 empty] | PERTH - December
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  | 0 | 88% | 94% | 98% | 100% | 99% | 95% | 89% | 81% | 72% | 61% |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 10 | 88% | 94% | 98% | 100% | 99% | 95% | 89% | 81% | 72% | 61% |  | 270 | 100% | 100% | 99% | 96% | 92% |  | 270 | 100% | 100% | 99% | 97% | 93% |  | 270 | 100% | 101% | 100% | 99% | 96% |  | 270 | 100% | 101% | 101% | 100% | 98% |  | 270 | 100% | 101% | 101% | 99% | 98% | 270 | 100% | 101% | 101% | 101% | 99% | 270 | 100% | 101% | 101% | 101% | 98% | 270 | 100% | 101% | 101% | 100% | 98% | 270 | 100% | 101% | 101% | 99% | 96% | 270 | 100% | 101% | 100% | 98% | 95% | 270 | 100% | 100% | 99% | 96% | 92% | 270 | 100% | 100% | 99% | 96% | 92%
|  | 20 | 88% | 94% | 98% | 99% | 98% | 94% | 89% | 81% | 72% | 62% |  | 280 | 100% | 100% | 99% | 96% | 92% |  | 280 | 100% | 101% | 100% | 98% | 95% |  | 280 | 100% | 102% | 103% | 103% | 100% |  | 280 | 100% | 104% | 105% | 106% | 105% |  | 280 | 100% | 104% | 107% | 108% | 108% | 280 | 100% | 105% | 108% | 110% | 110% | 280 | 100% | 104% | 107% | 109% | 109% | 280 | 100% | 104% | 106% | 106% | 106% | 280 | 100% | 102% | 104% | 103% | 101% | 280 | 100% | 102% | 102% | 100% | 98% | 280 | 100% | 100% | 99% | 97% | 93% | 280 | 100% | 100% | 98% | 95% | 92%
|  | 30 | 88% | 94% | 97% | 98% | 97% | 93% | 88% | 81% | 72% | 62% |  | 290 | 100% | 100% | 99% | 96% | 92% |  | 290 | 100% | 101% | 101% | 100% | 97% |  | 290 | 100% | 104% | 106% | 106% | 104% |  | 290 | 100% | 106% | 110% | 112% | 112% |  | 290 | 100% | 107% | 113% | 116% | 117% | 290 | 100% | 108% | 115% | 120% | 121% | 290 | 100% | 107% | 113% | 117% | 120% | 290 | 100% | 106% | 110% | 113% | 113% | 290 | 100% | 104% | 107% | 107% | 106% | 290 | 100% | 102% | 103% | 102% | 100% | 290 | 100% | 101% | 100% | 97% | 93% | 290 | 100% | 100% | 98% | 95% | 91%
|  | 40 | 88% | 93% | 96% | 96% | 95% | 92% | 86% | 80% | 71% | 62% |  | 300 | 100% | 100% | 99% | 96% | 92% |  | 300 | 100% | 102% | 102% | 101% | 98% |  | 300 | 100% | 105% | 108% | 109% | 108% |  | 300 | 100% | 108% | 113% | 117% | 118% |  | 300 | 100% | 110% | 118% | 124% | 126% | 300 | 100% | 112% | 121% | 129% | 133% | 300 | 100% | 111% | 119% | 126% | 129% | 300 | 100% | 109% | 114% | 119% | 120% | 300 | 100% | 105% | 109% | 110% | 110% | 300 | 100% | 103% | 104% | 104% | 102% | 300 | 100% | 101% | 100% | 98% | 93% | 300 | 100% | 100% | 98% | 95% | 90%
|  | 50 | 88% | 92% | 94% | 94% | 93% | 89% | 84% | 78% | 70% | 62% |  | 310 | 100% | 100% | 99% | 96% | 91% |  | 310 | 100% | 103% | 103% | 101% | 99% |  | 310 | 100% | 106% | 110% | 111% | 111% |  | 310 | 100% | 110% | 117% | 121% | 124% |  | 310 | 100% | 113% | 123% | 130% | 135% | 310 | 100% | 115% | 127% | 136% | 143% | 310 | 100% | 113% | 124% | 133% | 138% | 310 | 100% | 110% | 119% | 124% | 126% | 310 | 100% | 107% | 111% | 114% | 114% | 310 | 100% | 104% | 105% | 105% | 103% | 310 | 100% | 101% | 100% | 98% | 93% | 310 | 100% | 100% | 98% | 94% | 89%
|  | 60 | 88% | 91% | 93% | 93% | 90% | 87% | 82% | 76% | 69% | 61% |  | 320 | 100% | 100% | 99% | 96% | 90% |  | 320 | 100% | 103% | 104% | 102% | 99% |  | 320 | 100% | 107% | 112% | 114% | 113% |  | 320 | 100% | 112% | 120% | 125% | 128% |  | 320 | 100% | 115% | 127% | 137% | 143% | 320 | 100% | 118% | 133% | 144% | 152% | 320 | 100% | 116% | 129% | 139% | 146% | 320 | 100% | 112% | 121% | 128% | 131% | 320 | 100% | 108% | 113% | 116% | 117% | 320 | 100% | 104% | 106% | 106% | 104% | 320 | 100% | 101% | 100% | 97% | 93% | 320 | 100% | 100% | 98% | 93% | 88%
|  | 70 | 88% | 90% | 91% | 90% | 88% | 84% | 79% | 73% | 66% | 59% |  | 330 | 100% | 100% | 99% | 95% | 89% |  | 330 | 100% | 103% | 104% | 103% | 99% |  | 330 | 100% | 108% | 113% | 115% | 115% |  | 330 | 100% | 113% | 122% | 129% | 133% |  | 330 | 100% | 117% | 131% | 142% | 150% | 330 | 100% | 120% | 136% | 150% | 160% | 330 | 100% | 118% | 133% | 145% | 153% | 330 | 100% | 114% | 124% | 132% | 136% | 330 | 100% | 109% | 115% | 118% | 119% | 330 | 100% | 105% | 107% | 107% | 105% | 330 | 100% | 101% | 100% | 97% | 92% | 330 | 100% | 100% | 97% | 93% | 87%
|  | 80 | 88% | 89% | 89% | 88% | 85% | 81% | 76% | 70% | 63% | 56% |  | 340 | 100% | 100% | 99% | 94% | 88% |  | 340 | 100% | 103% | 104% | 103% | 99% |  | 340 | 100% | 108% | 114% | 116% | 116% |  | 340 | 100% | 113% | 124% | 132% | 136% |  | 340 | 100% | 118% | 134% | 146% | 154% | 340 | 100% | 121% | 140% | 155% | 166% | 340 | 100% | 119% | 136% | 149% | 158% | 340 | 100% | 114% | 126% | 135% | 140% | 340 | 100% | 109% | 116% | 120% | 121% | 340 | 100% | 105% | 107% | 107% | 105% | 340 | 100% | 101% | 100% | 97% | 92% | 340 | 100% | 100% | 97% | 92% | 85%
|  | 90 | 88% | 88% | 87% | 84% | 81% | 77% | 72% | 66% | 60% | 54% |  | 350 | 100% | 100% | 98% | 94% | 88% |  | 350 | 100% | 103% | 104% | 103% | 99% |  | 350 | 100% | 109% | 114% | 117% | 117% |  | 350 | 100% | 114% | 125% | 133% | 138% |  | 350 | 100% | 119% | 136% | 149% | 158% | 350 | 100% | 122% | 142% | 158% | 170% | 350 | 100% | 120% | 138% | 152% | 162% | 350 | 100% | 115% | 127% | 136% | 142% | 350 | 100% | 109% | 116% | 121% | 122% | 350 | 100% | 105% | 107% | 107% | 105% | 350 | 100% | 101% | 100% | 97% | 91% | 350 | 100% | 99% | 97% | 92% | 85%
|  | 100 | 88% | 87% | 85% | 81% | 77% | 73% | 68% | 62% | 56% | 50% |  | 0 | 100% | 100% | 98% | 94% | 87% |  | 0 | 100% | 103% | 104% | 103% | 99% |  | 0 | 100% | 109% | 114% | 117% | 117% |  | 0 | 100% | 114% | 125% | 133% | 138% |  | 0 | 100% | 119% | 136% | 150% | 159% | 0 | 100% | 122% | 143% | 159% | 171% | 0 | 100% | 121% | 138% | 153% | 163% | 0 | 100% | 115% | 128% | 137% | 143% | 0 | 100% | 110% | 117% | 121% | 122% | 0 | 100% | 105% | 107% | 107% | 105% | 0 | 100% | 101% | 100% | 96% | 91% | 0 | 100% | 99% | 96% | 92% | 84%
|  | 110 | 88% | 86% | 83% | 78% | 74% | 68% | 63% | 57% | 51% | 46% |  | 10 | 100% | 100% | 98% | 94% | 87% |  | 10 | 100% | 103% | 104% | 103% | 99% |  | 10 | 100% | 108% | 114% | 116% | 116% |  | 10 | 100% | 114% | 125% | 132% | 137% |  | 10 | 100% | 119% | 136% | 149% | 158% | 10 | 100% | 122% | 142% | 158% | 170% | 10 | 100% | 120% | 138% | 152% | 162% | 10 | 100% | 115% | 127% | 136% | 142% | 10 | 100% | 109% | 116% | 120% | 121% | 10 | 100% | 105% | 107% | 107% | 104% | 10 | 100% | 101% | 100% | 97% | 91% | 10 | 100% | 99% | 97% | 92% | 84%
|  | 120 | 88% | 85% | 81% | 75% | 69% | 63% | 58% | 52% | 47% | 42% |  | 20 | 100% | 100% | 98% | 94% | 88% |  | 20 | 100% | 103% | 104% | 103% | 99% |  | 20 | 100% | 108% | 113% | 115% | 115% |  | 20 | 100% | 113% | 123% | 130% | 135% |  | 20 | 100% | 118% | 134% | 146% | 155% | 20 | 100% | 121% | 140% | 155% | 166% | 20 | 100% | 119% | 136% | 149% | 158% | 20 | 100% | 114% | 126% | 134% | 140% | 20 | 100% | 109% | 115% | 119% | 120% | 20 | 100% | 105% | 107% | 107% | 104% | 20 | 100% | 101% | 100% | 97% | 92% | 20 | 100% | 100% | 97% | 92% | 85%
|  | 130 | 88% | 84% | 79% | 73% | 66% | 59% | 53% | 47% | 42% | 38% |  | 30 | 100% | 100% | 98% | 95% | 89% |  | 30 | 100% | 103% | 104% | 103% | 99% |  | 30 | 100% | 107% | 112% | 114% | 113% |  | 30 | 100% | 112% | 121% | 127% | 130% |  | 30 | 100% | 117% | 131% | 142% | 150% | 30 | 100% | 120% | 137% | 150% | 161% | 30 | 100% | 118% | 133% | 145% | 153% | 30 | 100% | 114% | 124% | 131% | 136% | 30 | 100% | 108% | 114% | 117% | 117% | 30 | 100% | 104% | 106% | 106% | 103% | 30 | 100% | 101% | 100% | 97% | 92% | 30 | 100% | 100% | 97% | 93% | 86%
|  | 140 | 88% | 83% | 77% | 70% | 62% | 55% | 48% | 42% | 38% | 33% |  | 40 | 100% | 100% | 98% | 95% | 90% |  | 40 | 100% | 103% | 103% | 102% | 98% |  | 40 | 100% | 106% | 110% | 112% | 111% |  | 40 | 100% | 111% | 119% | 124% | 126% |  | 40 | 100% | 115% | 127% | 138% | 143% | 40 | 100% | 118% | 133% | 145% | 152% | 40 | 100% | 116% | 129% | 139% | 146% | 40 | 100% | 111% | 121% | 127% | 131% | 40 | 100% | 107% | 113% | 115% | 115% | 40 | 100% | 104% | 105% | 105% | 102% | 40 | 100% | 101% | 100% | 97% | 93% | 40 | 100% | 100% | 97% | 93% | 88%
|  | 150 | 88% | 83% | 76% | 68% | 59% | 51% | 44% | 38% | 33% | 30% |  | 50 | 100% | 100% | 98% | 95% | 90% |  | 50 | 100% | 102% | 103% | 101% | 98% |  | 50 | 100% | 105% | 109% | 109% | 108% |  | 50 | 100% | 109% | 115% | 120% | 121% |  | 50 | 100% | 113% | 123% | 131% | 136% | 50 | 100% | 115% | 128% | 137% | 144% | 50 | 100% | 113% | 124% | 133% | 138% | 50 | 100% | 110% | 117% | 123% | 125% | 50 | 100% | 106% | 110% | 112% | 111% | 50 | 100% | 103% | 104% | 103% | 100% | 50 | 100% | 101% | 100% | 98% | 93% | 50 | 100% | 100% | 98% | 94% | 89%
|  | 160 | 88% | 82% | 75% | 66% | 57% | 48% | 40% | 34% | 30% | 27% |  | 60 | 100% | 100% | 99% | 95% | 91% |  | 60 | 100% | 102% | 102% | 100% | 97% |  | 60 | 100% | 104% | 106% | 106% | 105% |  | 60 | 100% | 107% | 112% | 115% | 115% |  | 60 | 100% | 110% | 118% | 124% | 127% | 60 | 100% | 112% | 121% | 129% | 134% | 60 | 100% | 111% | 120% | 126% | 129% | 60 | 100% | 108% | 114% | 118% | 119% | 60 | 100% | 105% | 108% | 109% | 108% | 60 | 100% | 102% | 103% | 102% | 99% | 60 | 100% | 101% | 100% | 98% | 93% | 60 | 100% | 100% | 98% | 94% | 90%
|  | 170 | 88% | 82% | 75% | 65% | 56% | 47% | 39% | 32% | 27% | 25% |  | 70 | 100% | 100% | 99% | 95% | 91% |  | 70 | 100% | 101% | 101% | 99% | 96% |  | 70 | 100% | 103% | 104% | 103% | 101% |  | 70 | 100% | 105% | 108% | 109% | 109% |  | 70 | 100% | 107% | 113% | 117% | 118% | 70 | 100% | 108% | 116% | 121% | 122% | 70 | 100% | 107% | 113% | 118% | 120% | 70 | 100% | 106% | 110% | 111% | 112% | 70 | 100% | 103% | 105% | 105% | 104% | 70 | 100% | 102% | 101% | 100% | 97% | 70 | 100% | 100% | 100% | 97% | 93% | 70 | 100% | 100% | 98% | 95% | 90%
|  | 180 | 88% | 82% | 74% | 65% | 55% | 46% | 38% | 31% | 26% | 24% |  | 80 | 100% | 100% | 98% | 95% | 91% |  | 80 | 100% | 101% | 100% | 98% | 94% |  | 80 | 100% | 101% | 101% | 100% | 97% |  | 80 | 100% | 102% | 104% | 104% | 102% |  | 80 | 100% | 104% | 107% | 109% | 108% | 80 | 100% | 106% | 108% | 111% | 111% | 80 | 100% | 104% | 107% | 110% | 110% | 80 | 100% | 103% | 105% | 106% | 105% | 80 | 100% | 102% | 102% | 101% | 99% | 80 | 100% | 101% | 100% | 98% | 95% | 80 | 100% | 100% | 99% | 96% | 93% | 80 | 100% | 100% | 98% | 95% | 91%
|  | 190 | 88% | 82% | 75% | 65% | 56% | 47% | 39% | 32% | 27% | 25% |  | 90 | 100% | 100% | 98% | 95% | 91% |  | 90 | 100% | 100% | 99% | 96% | 92% |  | 90 | 100% | 100% | 98% | 96% | 92% |  | 90 | 100% | 101% | 99% | 98% | 95% |  | 90 | 100% | 101% | 101% | 100% | 98% | 90 | 100% | 102% | 102% | 102% | 100% | 90 | 100% | 101% | 101% | 101% | 99% | 90 | 100% | 101% | 101% | 99% | 96% | 90 | 100% | 100% | 99% | 97% | 94% | 90 | 100% | 100% | 98% | 95% | 92% | 90 | 100% | 100% | 99% | 96% | 92% | 90 | 100% | 100% | 98% | 95% | 91%
|  | 200 | 88% | 82% | 75% | 66% | 57% | 49% | 41% | 34% | 30% | 27%
|  | 210 | 88% | 83% | 76% | 68% | 59% | 51% | 44% | 38% | 34% | 30%
|  | 220 | 88% | 84% | 77% | 70% | 63% | 55% | 49% | 43% | 38% | 34%
|  | 230 | 88% | 84% | 79% | 73% | 66% | 60% | 53% | 48% | 43% | 38%
|  | 240 | 88% | 85% | 81% | 75% | 70% | 64% | 58% | 53% | 48% | 43%
|  | 250 | 88% | 86% | 83% | 79% | 74% | 69% | 63% | 58% | 52% | 47%
|  | 260 | 88% | 88% | 85% | 82% | 78% | 73% | 68% | 63% | 56% | 50%
|  | 270 | 88% | 88% | 87% | 85% | 81% | 77% | 72% | 67% | 60% | 54%
|  | 280 | 88% | 89% | 89% | 88% | 85% | 81% | 76% | 70% | 64% | 57%
|  | 290 | 88% | 91% | 91% | 90% | 88% | 84% | 79% | 74% | 67% | 59%
|  | 300 | 88% | 92% | 93% | 93% | 91% | 87% | 82% | 76% | 69% | 61%
|  | 310 | 88% | 92% | 94% | 95% | 93% | 90% | 85% | 78% | 70% | 62%
|  | 320 | 88% | 93% | 96% | 97% | 95% | 92% | 87% | 80% | 71% | 62%
|  | 330 | 88% | 94% | 97% | 98% | 97% | 94% | 88% | 81% | 72% | 62%
|  | 340 | 88% | 94% | 98% | 99% | 98% | 94% | 89% | 81% | 72% | 62%
|  | 350 | 88% | 94% | 98% | 100% | 99% | 95% | 89% | 81% | 72% | 61%
CAIRNS
|  | 7.10 CAIRNS | [11 empty] | CAIRNS - Janurary | [6 empty] | CAIRNS - February | [6 empty] | CAIRNS - March | [6 empty] | CAIRNS - April | [6 empty] | CAIRNS - May | [5 empty] | CAIRNS - June | [5 empty] | CAIRNS - July | [5 empty] | CAIRNS - August | [5 empty] | CAIRNS - September | [5 empty] | CAIRNS - October | [5 empty] | CAIRNS - November | [5 empty] | CAIRNS - December
|  | Plane Azimuth (degrees) | Plane Inclination (degrees) 0: Plane Inclination (degrees) |  | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) | [5 empty] | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees) |  |  |  |  | Plane Azimuth (degrees) | Plane Inclination (degrees)
|  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40 |  | 0 | 10 | 20 | 30 | 40
|  | 0 | 95% | 99% | 100% | 99% | 96% | 90% | 82% | 73% | 62% | 52% |  | 270 | 100% | 100% | 98% | 95% | 90% |  | 270 | 100% | 100% | 98% | 95% | 91% |  | 270 | 100% | 100% | 99% | 97% | 93% |  | 270 | 100% | 101% | 101% | 98% | 95% |  | 270 | 100% | 101% | 100% | 98% | 94% | 270 | 100% | 101% | 100% | 98% | 96% | 270 | 100% | 101% | 100% | 98% | 95% | 270 | 100% | 101% | 100% | 98% | 94% | 270 | 100% | 100% | 100% | 97% | 93% | 270 | 100% | 101% | 100% | 97% | 93% | 270 | 100% | 101% | 99% | 96% | 92% | 270 | 100% | 100% | 99% | 96% | 91%
|  | 10 | 95% | 99% | 100% | 99% | 95% | 90% | 82% | 73% | 62% | 52% |  | 280 | 100% | 100% | 97% | 94% | 89% |  | 280 | 100% | 100% | 98% | 95% | 91% |  | 280 | 100% | 101% | 100% | 98% | 94% |  | 280 | 100% | 102% | 103% | 102% | 98% |  | 280 | 100% | 103% | 104% | 103% | 101% | 280 | 100% | 103% | 104% | 104% | 103% | 280 | 100% | 103% | 104% | 104% | 102% | 280 | 100% | 102% | 103% | 102% | 99% | 280 | 100% | 101% | 101% | 100% | 96% | 280 | 100% | 101% | 100% | 97% | 94% | 280 | 100% | 100% | 99% | 96% | 91% | 280 | 100% | 100% | 98% | 94% | 89%
|  | 20 | 95% | 98% | 100% | 98% | 95% | 90% | 82% | 73% | 63% | 53% |  | 290 | 100% | 99% | 97% | 93% | 87% |  | 290 | 100% | 100% | 98% | 95% | 90% |  | 290 | 100% | 101% | 101% | 100% | 96% |  | 290 | 100% | 103% | 105% | 104% | 103% |  | 290 | 100% | 104% | 107% | 108% | 107% | 290 | 100% | 106% | 109% | 110% | 109% | 290 | 100% | 105% | 108% | 110% | 109% | 290 | 100% | 104% | 106% | 106% | 104% | 290 | 100% | 102% | 103% | 101% | 99% | 290 | 100% | 101% | 100% | 98% | 94% | 290 | 100% | 100% | 98% | 94% | 90% | 290 | 100% | 99% | 96% | 92% | 87%
|  | 30 | 95% | 98% | 99% | 98% | 94% | 89% | 82% | 73% | 64% | 54% |  | 300 | 100% | 99% | 96% | 91% | 86% |  | 300 | 100% | 100% | 98% | 94% | 90% |  | 300 | 100% | 102% | 102% | 100% | 97% |  | 300 | 100% | 104% | 107% | 107% | 105% |  | 300 | 100% | 107% | 111% | 112% | 112% | 300 | 100% | 108% | 113% | 115% | 116% | 300 | 100% | 108% | 112% | 115% | 115% | 300 | 100% | 106% | 109% | 110% | 109% | 300 | 100% | 103% | 104% | 103% | 101% | 300 | 100% | 101% | 100% | 98% | 94% | 300 | 100% | 100% | 97% | 93% | 88% | 300 | 100% | 98% | 95% | 90% | 85%
|  | 40 | 95% | 98% | 99% | 97% | 94% | 88% | 81% | 73% | 64% | 55% |  | 310 | 100% | 98% | 95% | 90% | 83% |  | 310 | 100% | 100% | 98% | 94% | 89% |  | 310 | 100% | 102% | 103% | 101% | 98% |  | 310 | 100% | 105% | 109% | 110% | 108% |  | 310 | 100% | 108% | 114% | 117% | 117% | 310 | 100% | 109% | 116% | 120% | 121% | 310 | 100% | 109% | 116% | 120% | 120% | 310 | 100% | 107% | 111% | 113% | 113% | 310 | 100% | 104% | 106% | 105% | 103% | 310 | 100% | 101% | 100% | 98% | 93% | 310 | 100% | 99% | 96% | 92% | 86% | 310 | 100% | 98% | 94% | 89% | 82%
|  | 50 | 95% | 97% | 98% | 96% | 93% | 87% | 80% | 73% | 64% | 56% |  | 320 | 100% | 98% | 94% | 89% | 82% |  | 320 | 100% | 100% | 98% | 93% | 88% |  | 320 | 100% | 103% | 104% | 102% | 99% |  | 320 | 100% | 106% | 110% | 112% | 111% |  | 320 | 100% | 110% | 116% | 121% | 122% | 320 | 100% | 111% | 119% | 125% | 127% | 320 | 100% | 110% | 119% | 124% | 126% | 320 | 100% | 108% | 114% | 116% | 116% | 320 | 100% | 105% | 107% | 106% | 104% | 320 | 100% | 102% | 100% | 98% | 92% | 320 | 100% | 99% | 96% | 91% | 84% | 320 | 100% | 98% | 93% | 87% | 80%
|  | 60 | 95% | 97% | 97% | 95% | 91% | 86% | 79% | 72% | 64% | 56% |  | 330 | 100% | 98% | 93% | 87% | 80% |  | 330 | 100% | 100% | 98% | 93% | 87% |  | 330 | 100% | 103% | 104% | 103% | 99% |  | 330 | 100% | 107% | 111% | 113% | 112% |  | 330 | 100% | 111% | 119% | 124% | 126% | 330 | 100% | 113% | 122% | 128% | 132% | 330 | 100% | 112% | 121% | 127% | 130% | 330 | 100% | 109% | 115% | 119% | 119% | 330 | 100% | 105% | 108% | 108% | 105% | 330 | 100% | 101% | 100% | 97% | 92% | 330 | 100% | 99% | 95% | 90% | 82% | 330 | 100% | 97% | 92% | 85% | 77%
|  | 70 | 95% | 96% | 96% | 94% | 90% | 84% | 78% | 71% | 63% | 55% |  | 340 | 100% | 98% | 93% | 87% | 78% |  | 340 | 100% | 100% | 97% | 93% | 87% |  | 340 | 100% | 103% | 104% | 103% | 100% |  | 340 | 100% | 108% | 112% | 115% | 114% |  | 340 | 100% | 112% | 120% | 126% | 129% | 340 | 100% | 113% | 124% | 131% | 135% | 340 | 100% | 113% | 123% | 130% | 134% | 340 | 100% | 110% | 117% | 121% | 121% | 340 | 100% | 106% | 108% | 108% | 106% | 340 | 100% | 101% | 100% | 97% | 91% | 340 | 100% | 98% | 95% | 89% | 81% | 340 | 100% | 97% | 91% | 84% | 75%
|  | 80 | 95% | 96% | 95% | 92% | 88% | 82% | 76% | 69% | 62% | 54% |  | 350 | 100% | 97% | 93% | 86% | 77% |  | 350 | 100% | 100% | 97% | 92% | 86% |  | 350 | 100% | 104% | 105% | 103% | 100% |  | 350 | 100% | 108% | 113% | 115% | 115% |  | 350 | 100% | 112% | 121% | 128% | 131% | 350 | 100% | 114% | 125% | 133% | 138% | 350 | 100% | 113% | 124% | 131% | 135% | 350 | 100% | 110% | 117% | 122% | 123% | 350 | 100% | 106% | 109% | 109% | 106% | 350 | 100% | 101% | 100% | 96% | 90% | 350 | 100% | 98% | 94% | 88% | 80% | 350 | 100% | 96% | 91% | 83% | 74%
|  | 90 | 95% | 95% | 94% | 90% | 85% | 80% | 74% | 67% | 60% | 53% |  | 0 | 100% | 97% | 93% | 86% | 77% |  | 0 | 100% | 100% | 98% | 93% | 86% |  | 0 | 100% | 104% | 105% | 103% | 100% |  | 0 | 100% | 108% | 113% | 116% | 115% |  | 0 | 100% | 112% | 122% | 128% | 131% | 0 | 100% | 114% | 125% | 133% | 138% | 0 | 100% | 113% | 124% | 132% | 137% | 0 | 100% | 110% | 118% | 122% | 123% | 0 | 100% | 106% | 109% | 109% | 106% | 0 | 100% | 101% | 100% | 96% | 90% | 0 | 100% | 98% | 94% | 88% | 79% | 0 | 100% | 96% | 91% | 83% | 74%
|  | 100 | 95% | 95% | 92% | 89% | 83% | 78% | 71% | 64% | 58% | 51% |  | 10 | 100% | 98% | 93% | 87% | 78% |  | 10 | 100% | 100% | 98% | 93% | 87% |  | 10 | 100% | 104% | 105% | 103% | 100% |  | 10 | 100% | 108% | 113% | 115% | 115% |  | 10 | 100% | 112% | 121% | 128% | 131% | 10 | 100% | 114% | 125% | 133% | 138% | 10 | 100% | 113% | 124% | 131% | 135% | 10 | 100% | 110% | 117% | 122% | 123% | 10 | 100% | 106% | 109% | 109% | 106% | 10 | 100% | 101% | 100% | 96% | 90% | 10 | 100% | 98% | 94% | 88% | 79% | 10 | 100% | 96% | 91% | 83% | 74%
|  | 110 | 95% | 94% | 91% | 87% | 81% | 75% | 68% | 61% | 54% | 48% |  | 20 | 100% | 98% | 93% | 87% | 79% |  | 20 | 100% | 100% | 98% | 94% | 88% |  | 20 | 100% | 103% | 104% | 103% | 100% |  | 20 | 100% | 108% | 112% | 114% | 113% |  | 20 | 100% | 112% | 120% | 126% | 129% | 20 | 100% | 113% | 124% | 131% | 135% | 20 | 100% | 113% | 123% | 130% | 133% | 20 | 100% | 110% | 116% | 120% | 121% | 20 | 100% | 105% | 108% | 108% | 105% | 20 | 100% | 101% | 100% | 96% | 90% | 20 | 100% | 98% | 94% | 88% | 80% | 20 | 100% | 97% | 91% | 84% | 76%
|  | 120 | 95% | 94% | 90% | 85% | 79% | 72% | 65% | 58% | 51% | 45% |  | 30 | 100% | 98% | 94% | 88% | 81% |  | 30 | 100% | 100% | 98% | 94% | 89% |  | 30 | 100% | 103% | 104% | 103% | 99% |  | 30 | 100% | 106% | 111% | 112% | 111% |  | 30 | 100% | 111% | 119% | 124% | 125% | 30 | 100% | 112% | 121% | 128% | 131% | 30 | 100% | 112% | 121% | 127% | 130% | 30 | 100% | 109% | 115% | 118% | 119% | 30 | 100% | 105% | 107% | 107% | 104% | 30 | 100% | 101% | 99% | 96% | 90% | 30 | 100% | 98% | 95% | 89% | 82% | 30 | 100% | 97% | 92% | 85% | 78%
|  | 130 | 95% | 93% | 89% | 83% | 76% | 69% | 62% | 54% | 48% | 41% |  | 40 | 100% | 99% | 95% | 90% | 83% |  | 40 | 100% | 100% | 99% | 95% | 90% |  | 40 | 100% | 103% | 104% | 102% | 99% |  | 40 | 100% | 106% | 109% | 110% | 109% |  | 40 | 100% | 110% | 116% | 120% | 121% | 40 | 100% | 111% | 119% | 124% | 126% | 40 | 100% | 110% | 118% | 123% | 124% | 40 | 100% | 108% | 113% | 116% | 115% | 40 | 100% | 104% | 106% | 105% | 103% | 40 | 100% | 101% | 99% | 96% | 90% | 40 | 100% | 99% | 95% | 90% | 83% | 40 | 100% | 98% | 93% | 87% | 80%
|  | 140 | 95% | 93% | 88% | 82% | 74% | 66% | 58% | 50% | 44% | 38% |  | 50 | 100% | 99% | 96% | 91% | 86% |  | 50 | 100% | 100% | 99% | 96% | 91% |  | 50 | 100% | 102% | 103% | 101% | 98% |  | 50 | 100% | 105% | 108% | 108% | 106% |  | 50 | 100% | 108% | 113% | 116% | 117% | 50 | 100% | 109% | 116% | 119% | 121% | 50 | 100% | 109% | 115% | 119% | 120% | 50 | 100% | 107% | 111% | 112% | 112% | 50 | 100% | 103% | 105% | 104% | 101% | 50 | 100% | 100% | 99% | 96% | 90% | 50 | 100% | 99% | 96% | 91% | 85% | 50 | 100% | 98% | 94% | 89% | 82%
|  | 150 | 95% | 92% | 87% | 80% | 72% | 63% | 55% | 47% | 40% | 35% |  | 60 | 100% | 100% | 97% | 93% | 87% |  | 60 | 100% | 100% | 100% | 97% | 92% |  | 60 | 100% | 102% | 102% | 100% | 97% |  | 60 | 100% | 104% | 105% | 105% | 103% |  | 60 | 100% | 106% | 110% | 112% | 111% | 60 | 100% | 108% | 112% | 115% | 115% | 60 | 100% | 107% | 111% | 114% | 113% | 60 | 100% | 105% | 108% | 109% | 108% | 60 | 100% | 103% | 103% | 102% | 99% | 60 | 100% | 100% | 98% | 95% | 90% | 60 | 100% | 99% | 96% | 92% | 87% | 60 | 100% | 98% | 95% | 91% | 85%
|  | 160 | 95% | 92% | 87% | 79% | 71% | 61% | 52% | 45% | 38% | 33% |  | 70 | 100% | 100% | 98% | 94% | 90% |  | 70 | 100% | 100% | 100% | 97% | 93% |  | 70 | 100% | 101% | 101% | 100% | 96% |  | 70 | 100% | 103% | 103% | 103% | 100% |  | 70 | 100% | 104% | 107% | 107% | 106% | 70 | 100% | 105% | 108% | 109% | 108% | 70 | 100% | 105% | 108% | 109% | 107% | 70 | 100% | 104% | 105% | 105% | 103% | 70 | 100% | 102% | 102% | 100% | 97% | 70 | 100% | 100% | 98% | 95% | 90% | 70 | 100% | 100% | 97% | 93% | 88% | 70 | 100% | 99% | 96% | 92% | 87%
|  | 170 | 95% | 92% | 87% | 79% | 70% | 60% | 51% | 44% | 37% | 31% |  | 80 | 100% | 100% | 99% | 96% | 91% |  | 80 | 100% | 101% | 100% | 98% | 93% |  | 80 | 100% | 101% | 100% | 99% | 95% |  | 80 | 100% | 102% | 101% | 99% | 97% |  | 80 | 100% | 102% | 103% | 102% | 100% | 80 | 100% | 103% | 104% | 103% | 102% | 80 | 100% | 103% | 103% | 103% | 101% | 80 | 100% | 102% | 102% | 101% | 98% | 80 | 100% | 101% | 100% | 98% | 94% | 80 | 100% | 100% | 98% | 94% | 90% | 80 | 100% | 100% | 98% | 94% | 89% | 80 | 100% | 100% | 98% | 94% | 89%
|  | 180 | 95% | 92% | 86% | 79% | 69% | 60% | 51% | 43% | 36% | 31% |  | 90 | 100% | 101% | 100% | 97% | 93% |  | 90 | 100% | 101% | 100% | 98% | 94% |  | 90 | 100% | 100% | 99% | 97% | 93% |  | 90 | 100% | 101% | 99% | 96% | 92% |  | 90 | 100% | 101% | 99% | 97% | 94% | 90 | 100% | 101% | 100% | 97% | 94% | 90 | 100% | 101% | 99% | 97% | 94% | 90 | 100% | 100% | 99% | 96% | 93% | 90 | 100% | 100% | 98% | 95% | 91% | 90 | 100% | 100% | 98% | 94% | 90% | 90 | 100% | 100% | 98% | 95% | 91% | 90 | 100% | 100% | 99% | 96% | 91%
|  | 190 | 95% | 92% | 87% | 79% | 70% | 60% | 51% | 44% | 37% | 31%
|  | 200 | 95% | 92% | 87% | 80% | 71% | 62% | 53% | 45% | 38% | 33%
|  | 210 | 95% | 92% | 88% | 81% | 73% | 64% | 55% | 48% | 41% | 36%
|  | 220 | 95% | 93% | 88% | 82% | 75% | 67% | 59% | 51% | 45% | 39%
|  | 230 | 95% | 93% | 89% | 83% | 77% | 69% | 62% | 55% | 48% | 42%
|  | 240 | 95% | 94% | 90% | 85% | 79% | 73% | 65% | 59% | 52% | 46%
|  | 250 | 95% | 94% | 91% | 87% | 81% | 75% | 69% | 62% | 55% | 49%
|  | 260 | 95% | 95% | 93% | 89% | 84% | 78% | 72% | 65% | 58% | 51%
|  | 270 | 95% | 95% | 94% | 91% | 86% | 80% | 74% | 67% | 61% | 53%
|  | 280 | 95% | 96% | 95% | 92% | 88% | 83% | 76% | 69% | 62% | 55%
|  | 290 | 95% | 97% | 96% | 94% | 90% | 84% | 78% | 71% | 63% | 55%
|  | 300 | 95% | 97% | 97% | 95% | 91% | 86% | 79% | 72% | 64% | 56%
|  | 310 | 95% | 98% | 98% | 96% | 93% | 87% | 80% | 73% | 64% | 55%
|  | 320 | 95% | 98% | 99% | 97% | 94% | 88% | 81% | 73% | 64% | 55%
|  | 330 | 95% | 98% | 99% | 98% | 94% | 89% | 81% | 73% | 63% | 54%
|  | 340 | 95% | 98% | 100% | 98% | 95% | 90% | 82% | 73% | 63% | 53%
|  | 350 | 95% | 99% | 100% | 99% | 95% | 90% | 82% | 73% | 62% | 52%
Equipment
| Solar_Controllers | Brand | Pwr @ 12V | Pwr @ 24V | Pwr @ 36V | Pwr @ 48V | Voc max | Voc min | Vmpp min | System Voltage |  |  |  | PV max | Ibat max | Efficiency@12 | Efficiency@24 | Efficiency@36 | Efficiency@48
1 | Blue-/ SmartSolar MPPT 75/10 | Victron | 135 | 270 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 13 | 10 | 0.98 | 0.98 | 0 | 0
2 | Blue-/ SmartSolar MPPT 75/15 | Victron | 200 | 400 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 15 | 0.98 | 0.98 | 0 | 0
3 | Blue-/ SmartSolar MPPT 100/15 | Victron | 200 | 400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 15 | 0.98 | 0.98 | 0 | 0
4 | Smart Solar MPPT 100/20 | Victron | 290 | 580 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 20 | 20 | 0.98 | 0.98 | 0 | 0
5 | Smart Solar MPPT 100/20 48V | Victron | 0 | 0 | 0 | 1160 | 100 | 5 | 1 | N.A. | N.A. | N.A. | 48 | 20 | 20 | 0 | 0 | 0 | 0.98
6 | Blue-/ SmartSolar MPPT 100/30 | Victron | 440 | 880 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 30 | 30 | 0.98 | 0.98 | 0 | 0
7 | Blue-/ SmartSolar MPPT 100/50 | Victron | 700 | 1400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 50 | 50 | 0.98 | 0.98 | 0 | 0
8 | Blue-/ SmartSolar MPPT 150/35 | Victron | 500 | 1000 | 1500 | 2000 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 40 | 35 | 0.98 | 0.98 | 0.98 | 0.98
9 | Blue-/ SmartSolar MPPT 150/45 Tr/MC4 | Victron | 650 | 1300 |  | 2600 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 2600 | 45 | 0.98 | 0.98 | 0.98 | 0.98
10 | Blue-/ SmartSolar MPPT 150/60 Tr/MC4 | Victron | 860 | 1720 |  | 3440 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 50 | 60 | 0.98 | 0.98 | 0.98 | 0.98
11 | Blue-/ SmartSolar MPPT 150/70 Tr/Tr VE.Can/MC4 | Victron | 1000 | 2000 |  | 4000 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 50 | 70 | 0.98 | 0.98 | 0.98 | 0.98
12 | SmartSolar MPPT 150/85 Tr/MC4 | Victron | 1200 | 2400 |  | 4900 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 85 | 0.98 | 0.98 | 0.98 | 0.98
13 | SmartSolar MPPT 150/100 Tr/Tr VE.Can/MC4 | Victron | 1450 | 2900 |  | 5800 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 100 | 0.98 | 0.98 | 0.98 | 0.98
14 | SmartSolar MPPT 250/60 Tr/MC4 | Victron | 860 | 1720 |  | 3440 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 35 | 60 | 0.99 | 0.99 | 0.99 | 0.99
15 | SmartSolar MPPT 250/70 Tr/Tr VE.Can/MC4 | Victron | 1000 | 2000 |  | 4000 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 35 | 70 | 0.99 | 0.99 | 0.99 | 0.99
16 | SmartSolar MPPT 250/85 Tr/MC4 | Victron | 1200 | 2400 |  | 4900 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 85 | 0.99 | 0.99 | 0.99 | 0.99
17 | SmartSolar MPPT 250/100 Tr/Tr VE.Can/MC4 | Victron | 1450 | 2900 |  | 5800 | 250 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 100 | 0.99 | 0.99 | 0.99 | 0.99
18 | Fronius Primo 5KW Inverter | Fronius | Plane Inclination (degrees) 30: 6600; Plane Inclination (degrees) 40: 600 |  | 7500
19 | Fronius Primo 6KW Inverter | Fronius | Plane Inclination (degrees) 30: 6600; Plane Inclination (degrees) 40: 600
20 | SmartSolar MPPT 450/200 Tr | Victron | 1450 | 2900 |  | 11600 | 450 | 5 | 1 | 12 | 24 | 36 | 48 | 70 | 100 | 0.96 | 0.96 | 0.96 | 0.96
21 | SmartSolar MPPT 450/100 Tr | Victron | Plane Inclination (degrees) 30: 5800; Plane Inclination (degrees) 40: 450; Plane Inclination (degrees) 50: 5; Plane Inclination (degrees) 60: 1 | 48 | 8120 | 100 | 0.96 | 0.96 | 0.96 | 0.96
22 | Fronius Symo 5KW Inverter | Fronius | Plane Inclination (degrees) 30: 5000; Plane Inclination (degrees) 40: 600 |  | 10000 |  | 0.98 | 0.98 | 0.98 | 0.98
| Inverter_Chargers | Brand | Voltage | Power KVA | Power KW | Pmax KW | Chrg A | Max Inp A | Effic. % | Z.Load.W | AES W | Search W | Rem On | Grid Rdy | Length | Width.mm | Depth | Wt kg | Qty
2.4 | MultiplusII 48/3000/35 | Victron | 48 | 3000 | 2.4 | 5.5 | 35 | 32 | 0.95 | 11 | 7 | 2 | Yes | Yes | 499 | 268 | 141 | 18 | 1
4 | MultiplusII 48/5000/70 | Victron | 48 | 5000 | 4 | 9 | 35 | 50 | 0.96 | 18 | 12 | 2 | Yes | Yes | 560 | 320 | 141 | 29 | 1
1.2 | Phoenix 48/1200 | Victron | 48 | 1200 | 1.2 | 2.2 | 0 | 0 | 1 | 10 | 5 | 0 | Yes | No | 499 | 636 | 141 | 14 | 1
6.4 | Quattro 48/8000/100 | Victron | 48 | 8000 | 6.4 | 15 | 100 | 50 | 0.96 | 18 | 12 | 2 | Yes | Yes | 560 | 320 | 141 | 29 | 1
8 | MultiplusII 48/10000/100 | Victron | 48 | 10000 | 8 | 18 | 140 | 100 | 0.96 | 38 | 27 | 4 | Yes | Yes | 677 | 363 | 206 | 49 | 1
7.5 | Selectronic SP Pro 7.5KW | Selectronic | 48 | 7500 | 7.5 | 18 | 156 | 32.6 | 0.96 | 6 |  |  |  | Yes | 690 | 375 | 220 | 42 | 1
7.2 | MultiplusII 48/3000/35 x 3 | Victron | 48 | 9000 | 7.2 | 11 | 70 | 64 | 0.95 | 22 | 14 | 4 | Yes | Yes | 499 | 636 | 141 | 36 | 3
12 | MultiplusII 48/5000/70 x 3 | Victron | 48 | 15000 | 12 | 27 | 210 | 150 | 0.96 | 36 | 24 | 4 | Yes | Yes | 560 | 740 | 141 | 87 | 3
6.4 | MultiplusII 48/8000/100 | Victron | 48 | 8000 | 6.4 | 15 | 110 | 100 | 0.96 | 29 | 19 | 3 | Yes | No | 642 | 363 | 260 | 49 | 1
12 | Quattro 48/15000/110 | Victron | 48 | 15000 | 12 | 25 | 200 | 100 | 0.96 | 110 | 75 | 20 | Yes | No | 560 | 320 | 141 | 72 | 1
6 | Sunny Island 8.0H | SMA | 48 | 8000 | 6 | 11.5 | 140 | 100 | 0.96 | 29 |  |  | Yes | Yes | 612 | 467 | 242 | 63 | 1
| Battery_Modules | Voltage | Ah C20 | Ah C5 | Ah C10 | Terminals | Cycles @30% | Cycles @50% | Cycles @100% | Length | Width.mm | Height | Wgt kg | Max DOD | Max V | Nom C | Max C | Fault A | Chemistry
1 | Victron AGM Supercycle 60Ah | 12 | 60 | 52 | 56 | M5 | 1200 | 850 | 300 | 336 | 172 | 280 | 45 | 100% | 14.6 | 0.2 | 0.5 | 1785 | LeadCarbon
2 | Victron AGM Supercycle 100Ah | 12 | 100 | 82 | 90 | M8 | 1200 | 850 | 300 | 336 | 172 | 280 | 45 | 100% | 14.6 | 0.2 | 0.5 | 2815 | LeadCarbon
3 | Victron Lead Carbon 160Ah | 12 | 160 | 150 | 114 | M8 | 1200 | 850 | 300 | 336 | 172 | 280 | 45 | 100% | 14.6 | 0.2 | 0.5 | 5145 | LeadCarbon
4 | Victron AGM Supercycle 170Ah | 12 | 170 | 145 | 153 | M8 | 1200 | 850 | 300 | 336 | 172 | 280 | 45 | 100% | 14.6 | 0.2 | 0.5 | 4975 | AGM
5 | Victron AGM Supercycle 230Ah | 12 | 230 | 200 | 210 | M8 | 1200 | 850 | 300 | 336 | 172 | 280 | 45 | 100% | 14.6 | 0.2 | 0.5 | 6860 | AGM
6 | GNB 676Ah Gel | 2 | 624 | 524 | 543 | M10 | 4000 | 3200 | 2500 | 336 | 172 | 280 | 60 | 100% | 2.4 | 0.2 | 0.4 | 4050 | Gel
7 | HRESYS | 51 | 100 | 100 | 100 | M8 | 10000 | 6000 | 6000 | 570 | 420 | 132 | 35 | 100% | 58 | 0.5 | 1 | 200 | Lithium
8 | Powerhouse Lead-Carbon 100Ah | 12 | 100 | 83 | 90 | M6 | 1800 | 1500 | 1300 | 306 | 168 | 211 | 28 | 100% | 14.4 | 0.2 | 0.3 | 3500 | Carbon.AGM
9 | Powerhouse Lead-Carbon 120Ah | 12 | 120 | 95 | 90 | M6 | 1800 | 1500 | 1300 | 306 | 168 | 211 | 28 | 100% | 14.4 | 0.2 | 0.3 | 4200 | Carbon.AGM
10 | Powerhouse Lead-Carbon 200Ah | 12 | 218 | 184 | 200 | M8 | 1800 | 1500 | 1300 | 522 | 240 | 219 | 61 | 100% | 14.4 | 0.2 | 0.3 | 7000 | Carbon.AGM
11 | GenZ 3KWh Lithium Module | 52 | 57.8 | 58 | 58 | Anderson | 10000 | 10000 | 2500 | 570 | 420 | 88 | 35 | 100% | 58 | 0.5 | 1 | 200 | Lithium
12 | Powerplus eco 4.0KWh Lithium | 51.2 | 78 | 78 | 78 | Surlok |  | 10000 | 2700 | 635 | 434 | 88 | 41 | 80% | 56 | 0.5 | 0.80769 | 200 | Lithium
13 | Powerplus LiFe 3.3KWh Lithium | 51.2 | 64 | 64 | 64 | Surlok |  | 10000 | 2700 | 635 | 434 | 88 | 41 | 80% | 56 | 0.93 | 1.07 | 200 | Lithium
14 | GNB 1200Ah Gel | 2 | 958 | 795 | 895 | M10 | 4000 | 2600 | 1200 | 210 | 191 | 657 | 66.5 | 100% | 2.4 | 0.2 | 0.4 | 4550 | Gel
15 | Fusion 2V AGM 700Ah | 2 | 636 | 517 | 600 | M8 | 4000 | 2500 | 900 | 191 | 210 | 681 | 60 | 95% | 2.4 | 0.2 | 0.4 | 4300 | Gel
16 | BYD 5.0 Flex | 48 | 100 | 100 | 100 | M8 | 10000 | 3500 | 2000 | 442 | 450 | 132 | 32 | 98% | 54 | 0.5 | 1 | 2500 | Lithium
| Solar_Panels | Manuf'r | Part# | Power W | Vmpp V | Impp A | Voc V | Isc A | Effic. % | Fuse A | Pwr +/-.W | V temp coeff | Pmax temp coeff | Type | Type2 | Length | Width.mm | Thickness | Wgt kg
1 | Trina 415W Mono PERC | Trina | TSM-DE09R.08 | 415 | 41.7 | 9.94 | 50 | 10.55 | 20.8 | 20 | 5 | -0.25 | -0.34 | Mono | PERC | 1762 | 1134 | 30 | 21.8
2 | Trina 400W Mono PERC | Trina | TSM-DE09.08 | 400 | 34.2 | 11.7 | 41.2 | 12.28 | 21.1 | 20 | 5 | -0.25 | -0.34 | Mono | PERC | 1754 | 1096 | 30 | 21
3 | ET Solar | Trina | ET-P660255BB | 255 | 30.29 | 8.42 | 37.89 | 9 | 15.67 | 15 | 5 | -0.129 | -0.3 | Mono | PERC | 1698 | 1004 | 35 | 18.7
4 | Seraphim 400W Mono PERC | Seraphim | sRP-400-BMA-HV | 400 | 41.6 | 9.62 | 49.1 | 10.1 | 19.81 | 20 | 5 | -0.28 | -0.3 | Mono | PERC | 2015 | 1002 | 40 | 23
5 | Seraphim 3300W Mono PERC | Seraphim | sRP-400-BMA-HV | 330 | 34.4 | 9.6 | 40.8 | 10.11 | 19.49 | 20 | 5 | -0.28 | -0.3 | Mono | PERC | 1690 | 1002 | 35 | 19
6 | 190W Mono | Suntech | STP 190W | 190 | 36 | 8.1 | 44 | 5.7 | 15 | 15 | 5 | -0.28 | -0.3 | Mono | PERC | 1580 | 808 | 35 | 16
7 | Trina 390W Mono PERC | Trina | TSM-390DE09.05 | 390 | 33.8 | 11.54 | 40.8 | 12.14 | 20.3 | 20 | 5 | -0.25 | -0.3 | Mono | PERC | 1754 | 1096 | 30 | 21
8 | Trina 415W Mono PERC | Trina | TSM-DE09.08R | 415 | 41.7 | 9.94 | 50 | 10.55 | 20.8 | 20 | 5 | -0.25 | -0.34 | Mono | PERC | 1762 | 1134 | 30 | 22
9 | Trina 250W Mono | Trina | TSM-250PC05A | 250 | 30.3 | 8.27 | 38 | 8.79 | 15.3 | 15 | 5 | -0.32 | -0.3 | Mono |  | 1650 | 941 | 40 | 19.5
10 | Sunpower 410W Mono PERC | Sunpower | P3-410-COM-1500 | 410 | 44.5 | 9.21 | 53.9 | 9.89 | 19.9 | 18 | 5 | -0.29 | -0.3 | Mono | PERC | 2066 | 998 | 40 | 22.3
Equipment-Options
| Solar_Arrays | Panel # | Panel W | Panels/St | Strings | Pnl Qty | Array W | Array W | Vmpp V | Impp A | Voc V | Isc A | Effic. % | Fuse A | Pwr +/-.W | V temp coeff | I temp coeff | STC C | Length | Width.mm | Thickness | Wgt kg | Strg VOC | MPPT | SC Qty
1 | 0
2 | 1.5 | 9 | 250 | 3 | 2 | 6 | 1500 | 9000 | 30.3 | 8.27 | 38 | 8.79 | 15.3 | 15 | 5 | -0.32 | -0.3 | 25 | 1650 | 941 | 40 | 19.5 | 114 | 18 | 1
3 | 3.2 | 2 | 400 | 8 | 1 | 8 | 3200 | 25600 | 34.2 | 11.7 | 41.2 | 12.28 | 21.1 | 20 | 5 | -0.25 | -0.34 | 25 | 1754 | 1096 | 30 | 21 | 329.6 | 13 | 1
4 | 3.8 | 6 | 190 | 2 | 10 | 20 | 3800 | 76000 | 36 | 8.1 | 44 | 5.7 | 15 | 15 | 5 | -0.28 | -0.3 | 25 | 1580 | 808 | 35 | 16 | 88 | 13 | 1
5 | 4.08 | 3 | 255 | 4 | 4 | 16 | 4080 | 65280 | 30.29 | 8.42 | 37.89 | 9 | 15.67 | 15 | 5 | -0.129 | -0.3 | 25 | 1698 | 1004 | 35 | 18.7 | 151.56 | 16 | 1
6 | 4.92 | 10 | 410 | 6 | 2 | 12 | 4920 | 59040 | 44.5 | 9.21 | 53.9 | 9.89 | 19.9 | 18 | 5 | -0.29 | -0.3 | 25 | 2066 | 998 | 40 | 22.3 | 323.4 | 18 | 1
7 | 5.6 | 2 | 400 | 7 | 2 | 14 | 5600 | 78400 | 34.2 | 11.7 | 41.2 | 12.28 | 21.1 | 20 | 5 | -0.25 | -0.34 | 25 | 1754 | 1096 | 30 | 21 | 288.4 | 21 | 1
8 | 6.64 | 1 | 415 | 8 | 2 | 16 | 6640 | 106240 | 41.7 | 9.94 | 50 | 10.55 | 20.8 | 20 | 5 | -0.25 | -0.34 | 25 | 1762 | 1134 | 30 | 21.8 | 400 | 21 | 1
9 | 7.2 | 2 | 400 | 9 | 2 | 18 | 7200 | 129600 | 34.2 | 11.7 | 41.2 | 12.28 | 21.1 | 20 | 5 | -0.25 | -0.34 | 25 | 1754 | 1096 | 30 | 21 | 370.8 | 21 | 1
10 | 8 | 2 | 400 | 10 | 2 | 20 | 8000 | 160000 | 34.2 | 11.7 | 41.2 | 12.28 | 21.1 | 20 | 5 | -0.25 | -0.34 | 25 | 1754 | 1096 | 30 | 21 | 412 | 22 | 1
11 | 10.53 | 2 | 390 | 9 | 3 | 27 | 10530 | 284310 | 34.2 | 11.7 | 41.2 | 12.28 | 21.1 | 20 | 5 | -0.25 | -0.34 | 25 | 1754 | 1096 | 30 | 21 | 370.8 | 20 | 1
12 | 12.45 | 1 | 415 | 5 | 6 | 30 | 12450 | 373500 | 41.7 | 9.94 | 50 | 10.55 | 20.8 | 20 | 5 | -0.25 | -0.34 | 25 | 1762 | 1134 | 30 | 21.8 | 250 | 16 | 2
13 | 14.04 | 1 | 390 | 9 | 4 | 36 | 14040 | 505440 | 41.7 | 9.94 | 50 | 10.55 | 20.8 | 20 | 5 | -0.25 | -0.34 | 25 | 1762 | 1134 | 30 | 21.8 | 450 | 20 | 1
| Battery_Banks | Module# | Batt Ah | Mods/St | Strings | Mod V | String V | Bank AH | Mod Type | Qty | DOD
1 | 2.88 | 1 | 60 | 4 | 1 | 12 | 48 | 2880 | LeadCarbon | 4 | 100%
2 | 4.8 | 8 | 100 | 4 | 1 | 12 | 48 | 4800 | Carbon.AGM | 4 | 100%
3 | 7.68 | 3 | 160 | 4 | 1 | 12 | 48 | 7680 | LeadCarbon | 4 | 100%
4 | 7.9872 | 12 | 78 | 1 | 2 | 51.2 | 51.2 | 7987.2 | Lithium | 2 | 100%
5 | 8.16 | 4 | 170 | 4 | 1 | 12 | 48 | 8160 | AGM | 4 | 100%
6 | 9.8304 | 13 | 64 | 1 | 3 | 51.2 | 51.2 | 9830.4 | Lithium | 3 | 100%
7 | 11.04 | 5 | 230 | 4 | 1 | 12 | 48 | 11040 | AGM | 4 | 100%
8 | 12.0224 | 11 | 57.8 | 1 | 4 | 52 | 52 | 12022.4 | Lithium | 4 | 100%
9 | 14.4 | 2 | 100 | 4 | 3 | 12 | 48 | 14400 | LeadCarbon | 12 | 100%
10 | 15.028 | 11 | 57.8 | 1 | 5 | 52 | 52 | 15028 | Lithium | 5 | 100%
11 | 18.0336 | 11 | 57.8 | 1 | 6 | 52 | 52 | 18033.6 | Lithium | 6 | 100%
12 | 20 | 16 | 100 | 1 | 4 | 50 | 50 | 20000 | Lithium | 4 | 98%
13 | 21.0392 | 11 | 57.8 | 1 | 7 | 52 | 52 | 21039.2 | Lithium | 7 | 100%
14 | 24.0448 | 11 | 57.8 | 1 | 8 | 52 | 52 | 24044.8 | Lithium | 8 | 100%
15 | 29.952 | 6 | 624 | 24 | 1 | 2 | 48 | 29952 | Gel | 24 | 100%
16 | 27.0504 | 11 | 57.8 | 1 | 9 | 52 | 52 | 27050.4 | Lithium | 9 | 100%
17 | 30.056 | 11 | 57.8 | 1 | 10 | 52 | 52 | 30056 | Lithium | 10 | 100%
User Profiles
| Users: | Profile | Plane Inclination (degrees) 0: KWh/day; Plane Inclination (degrees) 10: KW.max
1 | 2 | 2 PPl | Plane Inclination (degrees) 0: 9; Plane Inclination (degrees) 10: 4
2 | 3 | 3 PPl | Plane Inclination (degrees) 0: 14; Plane Inclination (degrees) 10: 4
3 | 4-5 | 4-5 Ppl | Plane Inclination (degrees) 0: 19; Plane Inclination (degrees) 10: 5
4 | 5+ | LargeUser | Plane Inclination (degrees) 0: 26; Plane Inclination (degrees) 10: 6.5
5 | High Use | V.HighUser | Plane Inclination (degrees) 0: 35; Plane Inclination (degrees) 10: 8
|  | SpecifyLoads>> | Plane Inclination (degrees) 10: Loads.Sheet